## Macros
Bureau of Reclamation
Section 1834 Energy Analysis - Version 1.06 |  | Read and Follow the Below Directions
Facility Name | Generic Federal Dam
Agency
Analysis Performed by
Tailrace Elevation (MSL) in feet | 1234.56
Exceedance Chart Maximum (CFS) | 900
Exceedance Chart Grid Step (CFS) | 50
Data Minimum - Project Head (ft) | 0
Data Maximum - Project Head (ft) | 0
Minimum Turbine Head (ft) | 125
Maximum Turbine Head (ft) | 250
Minimum Turbine Flow (CFS) | 100
Maximum Turbine Flow (CFS) | 500
Expected Power Rate ($/KWH) | 0.052
Note - Yellow boxes are user entries
Analysis Results
Data Set (Years) | 0
Projected Annual Production (KWH) | #REF!
Projected Annual Revenue | #REF!
Turbine Peak Power (KW) | #REF!
Plant Factor | 0
Note - Use the below button to print analysis results
(Do not use print bottons at top of screen !!!
For help contact:
Robert W. Ross, P.E.
Pacific Northwest Region
Bureau of Reclamation
(208) 378-5332
rross@pn.usbr.gov
1. Start by entering in Project upstream water elevation and project outflow in "Input Data" tab. 2. Manually scan the input data for bad data points or missing data. 3. Enter tailrace outlet works elevation or expected average elevation (Cell B7) 4. Press the below "Preprocess" Data button - This completes and formats data in "Input Data" tab
6. Seach for bad data by clicking on Input Data tab then click on Tools > Error Check at top of page. 7. Press the below "Produce Exceedence Chart" 8. Review sorted data in "Flow Exceedence" tab. Bad data points will appear at the top of list or bottom of the list. If bad data points are found, note the date, go back into the "Input Data" tab, correct the appropriate flows and and press the below button again to produce a new Exceedence Chart
9. If all data looks good proceed to the next step. 10. Review the values for data minimum and maximum head (Cell B14 and B15) Enter in values for Turbine Minimum and Maximum Head. Power output will be zero for values above maximum head (flood flows) and zero for values below minimum head. A good value for minimum head is 25% of the maximum head. 11. Examine the Exceedence graph. Decide on a maximum rated turbine flow. Generally this is sized at about 20% exceedence. Enter this value in cell B19. 12. Decide on a minimum turbine flow. Generally this is about 10% of maximum flow. Enter this value in cell B20. 13. Press the below button to complete the energy analysis.
14. Review calculation results on this sheet 15. Click on "File" > "Save As" > Enter new file name and save

## Input Data
Generic Federal Dam | [6 empty] | Generic Federal Dam
Data Source -
Date | Head Water Elevation (ft) | Tailwater (Project Data Book) | Net head (feet) | Flow (CFS) | Max Available Power (KW) Hd * Q *.073
Plant sizing based 29 Years of Data (1976-2005)
Plant Capacity Sized at 20% Flow Exceedance
[6 empty] | Projected Annual Production (kwh) |  |  | 21790317.9419
[6 empty] | Projected Annual Revenue (.06 / KWH) |  |  | 1307419.0765
[6 empty] | Turbine Peak Power (KW) |  |  | 4847.55
[6 empty] | Plant Factor |  |  | 0.5129
(See Annual Revenue tab for calculation of above numbers
[6 empty] | Max Head (ft) |  | 190.1
[6 empty] | Min Head(ft) |  | 47.525
[6 empty] | Max Flow (cfs) |  | 340
[6 empty] | Min Flow (cfs) |  | 34
Conclusions:

## Flow Exceedence
Generic Federal Dam
Flow (CFS) | Date | Head Water Elevation (ft) | Tailwater (Project Data Book) | Net head (feet) | Flow (CFS) | Power (KW) Hd * Q *.075 | Point Counter | % Exceedence
[9 empty] | Size Plant at | 20% | Exceedence = | CFS
Input Data Min / Max Values
[9 empty] | Max Head (ft) | 2008.14
[9 empty] | Min Head(ft) | 1927.72
[9 empty] | Max Flow (cfs) | 3280
[9 empty] | Min Flow (cfs) | 7.1

## Power Exceedence
| Generic Federal Dam |  |  |  |  | Power Exceedence
Power (KW) Hd * Q *.075 | Date | Head Water Elevation (ft) | Tailwater (Project Data Book) | Net head (feet) | Flow (CFS) | Power (KW) Hd * Q *.073 | Point Counter | % Exceedence
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis

## Net Head Exceedence
Generic Federal Dam
Net head (feet) | Date | Head Water Elevation (ft) | Tailwater (Project Data Book) | Net head (feet) | Flow (CFS) | Power (KW) Hd * Q *.073 | Point Counter | % Exceedence
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis
Plant sizing basis

## Annual Revenue
|  |  | Generic Federal Dam | Max Flow Size - |  |  | 250 | CFS - Revenue Calculations
[5 empty] | 250 CFS | 25 CFS | 250 Ft | 25 Ft
Date | Head Water Elevation (ft) | Tailwater MSL | Net head (feet) | Flow (CFS) | Max Flow Limit | Min Flow Limit | Max Head Limit | Min Head Limit | Generation Head (ft) | Generation Flow (CFS) | Power (KW) Hd * Q *.073 | Day Energy (KWH)
[13 empty] | Plant Flow Capacity (CFS) |  | 500
[13 empty] | Total Period Energy (KWH) |  | #REF!
[13 empty] | Projected Annual Production (kwh) |  | #REF!
[13 empty] | Projected Annual Revenue @ .052$/KWH |  | #REF!
[13 empty] | Turbine Peak Power (KW) |  | #REF!
[13 empty] | Plant Factor |  | 0
[13 empty] | Data Years - | 0

## Templates
Input Data Min / Max Values
Date | Head Water Elevation (ft) | Blank Column | Blank Column | Flow (CFS) | User Entry - Project Information |  | Max Head (ft) | 0
2005-09-30 | 3214.34 |  |  | 171.23 |  |  | Min Head(ft) | 0
2005-09-29 | 3216.84 |  |  | 183.13 | Project Name | A.R. Bowman Dam | Max Flow (cfs) | 0
2005-09-28 | 3214.67 |  |  | 183.13 |  |  | Min Flow (cfs) | 0
2005-09-27 | 3214.84 |  |  | 183.13 | Tailrace Elevation (MSL) in feet | 3052.6
2005-09-26 | 3214.99 |  |  | 183.13
2005-09-25 | 3215.14 |  |  | 184.21 | Exceedance Chart Maximum (CFS) | 1000
2005-09-24 | 3215.3 |  |  | 185.07 | Exceedance Chart Grid Step (CFS) | 50
2005-09-23 | 3215.46 |  |  | 190.18
2005-09-22 | 3215.65 |  |  | 197.98 | Mimimum Turbine Head (ft) | 50
2005-09-21 | 3215.85 |  |  | 197.98 | Maximum Turbine Head (ft) | 195
2005-09-20 | 3216.04 |  |  | 199.71
2005-09-19 | 3216.24 |  |  | 199.8 | Minimum Turbine Flow (ft) | 34
2005-09-18 | 3216.39 |  |  | 199.8 | Maximum Turbine Flow (ft) | 350
2005-09-17 | 3216.56 |  |  | 199.8
2005-09-16 | 3216.73 |  |  | 208.42 | Expected Power Rate ($/KWH) | 0.06
2005-09-15 | 3216.92 |  |  | 223.36
2005-09-14 | 3217.12 |  |  | 223.51
2005-09-13 | 3217.32 |  |  | 223.47
2005-09-12 | 3217.52 |  |  | 224.12
2005-09-11 | 3217.72 |  |  | 224.26
2005-09-10 | 3217.92 |  |  | 224.26
2005-09-09 | 3218.14 |  |  | 224.26
2005-09-08 | 3218.41 |  |  | 224.26
2005-09-07 | 3218.59 |  |  | 224.26
2005-09-06 | 3218.8 |  |  | 224.26
2005-09-05 | 3218.98 |  |  | 224.26
2005-09-04 | 3219.18 |  |  | 224.26
2005-09-03 | 3219.39 |  |  | 224.26
2005-09-02 | 3219.61 |  |  | 224.26
2005-09-01 | 3219.83 |  |  | 224.26
2005-08-31 | 3220.03 |  |  | 224.26
2005-08-30 | 3220.22 |  |  | 224.26
2005-08-29 | 3220.38 |  |  | 224.26
2005-08-28 | 3220.64 |  |  | 224.26
2005-08-27 | 3220.83 |  |  | 224.26
2005-08-26 | 3221.04 |  |  | 224.26
2005-08-25 | 3221.24 |  |  | 224.26
2005-08-24 | 3221.43 |  |  | 224.26
2005-08-23 | 3221.63 |  |  | 224.26
2005-08-22 | 3221.86 |  |  | 224.26
2005-08-21 | 3222.1 |  |  | 224.26
2005-08-20 | 3222.27 |  |  | 224.26
2005-08-19 | 3222.45 |  |  | 224.26
2005-08-18 | 3222.63 |  |  | 224.26
2005-08-17 | 3222.82 |  |  | 224.3
2005-08-16 | 3223.01 |  |  | 224.7
2005-08-15 | 3223.21 |  |  | 226.03
2005-08-14 | 3223.39 |  |  | 226.2
2005-08-13 | 3223.59 |  |  | 226.2
2005-08-12 | 3223.79 |  |  | 226.2
2005-08-11 | 3223.99 |  |  | 226.2
2005-08-10 | 3224.19 |  |  | 226.2
2005-08-09 | 3224.41 |  |  | 226.2
2005-08-08 | 3224.62 |  |  | 226.22
2005-08-07 | 3224.81 |  |  | 226.2
2005-08-06 | 3225.01 |  |  | 226.2
2005-08-05 | 3225.21 |  |  | 226.2
2005-08-04 | 3225.39 |  |  | 226.95
2005-08-03 | 3225.57 |  |  | 228.23
2005-08-02 | 3225.73 |  |  | 228.23
2005-08-01 | 3225.93 |  |  | 228.23
2005-07-31 | 3226.17 |  |  | 228.23
2005-07-30 | 3226.35 |  |  | 228.23
2005-07-29 | 3226.53 |  |  | 228.23
2005-07-28 | 3226.71 |  |  | 228.23
2005-07-27 | 3226.89 |  |  | 228.23
2005-07-26 | 3227.05 |  |  | 228.23
2005-07-25 | 3227.23 |  |  | 228.23
2005-07-24 | 3227.44 |  |  | 228.23
2005-07-23 | 3227.65 |  |  | 228.23
2005-07-22 | 3227.85 |  |  | 228.3
2005-07-21 | 3228.01 |  |  | 228.23
2005-07-20 | 3228.19 |  |  | 228.23
2005-07-19 | 3228.38 |  |  | 228.23
2005-07-18 | 3228.54 |  |  | 228.23
2005-07-17 | 3228.69 |  |  | 228.25
2005-07-16 | 3228.85 |  |  | 228.34
2005-07-15 | 3229.07 |  |  | 228.23
2005-07-14 | 3229.21 |  |  | 228.23
2005-07-13 | 3229.37 |  |  | 228.23
2005-07-12 | 3229.52 |  |  | 228.23
2005-07-11 | 3229.68 |  |  | 234.54
2005-07-10 | 3229.81 |  |  | 241.07
2005-07-09 | 3229.96 |  |  | 241.64
2005-07-08 | 3230.13 |  |  | 242.56
2005-07-07 | 3230.32 |  |  | 242.73
2005-07-06 | 3230.48 |  |  | 242.75
2005-07-05 | 3230.66 |  |  | 242.73
2005-07-04 | 3230.78 |  |  | 242.73
2005-07-03 | 3230.92 |  |  | 242.73
2005-07-02 | 3231.08 |  |  | 242.73
2005-07-01 | 3231.26 |  |  | 242.73
2005-06-30 | 3231.4 |  |  | 242.73
2005-06-29 | 3231.52 |  |  | 242.73
2005-06-28 | 3231.66 |  |  | 242.73
2005-06-27 | 3231.79 |  |  | 242.73
2005-06-26 | 3231.92 |  |  | 242.73
2005-06-25 | 3232.07 |  |  | 242.73
2005-06-24 | 3232.2 |  |  | 242.73
2005-06-23 | 3232.32 |  |  | 242.73
2005-06-22 | 3232.44 |  |  | 242.73
2005-06-21 | 3232.58 |  |  | 242.73
2005-06-20 | 3232.7 |  |  | 242.73
2005-06-19 | 3232.76 |  |  | 242.73
2005-06-18 | 3232.86 |  |  | 242.75
2005-06-17 | 3232.99 |  |  | 242.73
2005-06-16 | 3233.1 |  |  | 242.82
2005-06-15 | 3233.23 |  |  | 242.73
2005-06-14 | 3233.34 |  |  | 242.73
2005-06-13 | 3233.47 |  |  | 242.73
2005-06-12 | 3233.59 |  |  | 242.73
2005-06-11 | 3233.69 |  |  | 242.73
2005-06-10 | 3233.82 |  |  | 242.73
2005-06-09 | 3233.92 |  |  | 242.73
2005-06-08 | 3234.01 |  |  | 242.73
2005-06-07 | 3234.1 |  |  | 242.73
2005-06-06 | 3234.19 |  |  | 245.03
2005-06-05 | 3234.28 |  |  | 251.25
2005-06-04 | 3234.4 |  |  | 251.23
2005-06-03 | 3234.48 |  |  | 256.89
2005-06-02 | 3234.55 |  |  | 266.89
2005-06-01 | 3234.64 |  |  | 271
2005-05-31 | 3234.72 |  |  | 275.38
2005-05-30 | 3234.83 |  |  | 287.41
2005-05-29 | 3234.9 |  |  | 287.5
2005-05-28 | 3234.93 |  |  | 287.48
2005-05-27 | 3234.96 |  |  | 289.87
2005-05-26 | 3234.95 |  |  | 344.56
2005-05-25 | 3234.96 |  |  | 394.52
2005-05-24 | 3234.96 |  |  | 461.35
2005-05-23 | 3234.98 |  |  | 632.78
2005-05-22 | 3235.03 |  |  | 760.54
2005-05-21 | 3235.07 |  |  | 856.24
2005-05-20 | 3235.11 |  |  | 968.86
2005-05-19 | 3235.18 |  |  | 1027.73
2005-05-18 | 3235.18 |  |  | 1002.47
2005-05-17 | 3235.16 |  |  | 778.58
2005-05-16 | 3234.96 |  |  | 570.92
2005-05-15 | 3234.84 |  |  | 581.48
2005-05-14 | 3234.87 |  |  | 648.53
2005-05-13 | 3234.91 |  |  | 717.37
2005-05-12 | 3234.91 |  |  | 760.34
2005-05-11 | 3234.9 |  |  | 759.94
2005-05-10 | 3234.88 |  |  | 737.58
2005-05-09 | 3234.88 |  |  | 649.95
2005-05-08 | 3234.92 |  |  | 722.62
2005-05-07 | 3234.98 |  |  | 794.88
2005-05-06 | 3235.04 |  |  | 796.85
2005-05-05 | 3235.08 |  |  | 711.32
2005-05-04 | 3235.13 |  |  | 670.95
2005-05-03 | 3235.18 |  |  | 674.85
2005-05-02 | 3235.28 |  |  | 679.66
2005-05-01 | 3235.32 |  |  | 707.25
2005-04-30 | 3235.37 |  |  | 816.34
2005-04-29 | 3235.46 |  |  | 1075.24
2005-04-28 | 3235.59 |  |  | 1388.94
2005-04-27 | 3235.88 |  |  | 1264.69
2005-04-26 | 3236.06 |  |  | 875.76
2005-04-25 | 3235.82 |  |  | 615.73
2005-04-24 | 3235.56 |  |  | 492.86
2005-04-23 | 3235.2 |  |  | 344.01
2005-04-22 | 3234.95 |  |  | 251.2
2005-04-21 | 3234.77 |  |  | 244.84
2005-04-20 | 3234.63 |  |  | 244.84
2005-04-19 | 3234.51 |  |  | 244.82
2005-04-18 | 3234.34 |  |  | 244.84
2005-04-17 | 3234.11 |  |  | 244.84
2005-04-16 | 3233.96 |  |  | 244.84
2005-04-15 | 3233.86 |  |  | 235.42
2005-04-14 | 3233.74 |  |  | 226.2
2005-04-13 | 3233.6 |  |  | 226.2
2005-04-12 | 3233.55 |  |  | 226.2
2005-04-11 | 3233.32 |  |  | 214.7
2005-04-10 | 3233.12 |  |  | 85.14
2005-04-09 | 3232.76 |  |  | 69.09
2005-04-08 | 3232.32 |  |  | 69.09
2005-04-07 | 3231.78 |  |  | 68.62
2005-04-06 | 3231.28 |  |  | 68.26
2005-04-05 | 3230.87 |  |  | 67.98
2005-04-04 | 3230.44 |  |  | 67.98
2005-04-03 | 3229.99 |  |  | 68
2005-04-02 | 3229.62 |  |  | 67.98
2005-04-01 | 3229.21 |  |  | 67.98
2005-03-31 | 3228.74 |  |  | 67.98
2005-03-30 | 3228.22 |  |  | 67.98
2005-03-29 | 3227.53 |  |  | 67.56
2005-03-28 | 3226.67 |  |  | 67.16
2005-03-27 | 3225.64 |  |  | 66.9
2005-03-26 | 3225.23 |  |  | 66.87
2005-03-25 | 3224.9 |  |  | 66.87
2005-03-24 | 3224.52 |  |  | 66.87
2005-03-23 | 3224.06 |  |  | 66.87
2005-03-22 | 3223.56 |  |  | 66.87
2005-03-21 | 3223.13 |  |  | 66.87
2005-03-20 | 3222.6 |  |  | 66.89
2005-03-19 | 3222.04 |  |  | 66.87
2005-03-18 | 3221.6 |  |  | 66.38
2005-03-17 | 3221.2 |  |  | 66.12
2005-03-16 | 3220.82 |  |  | 65.86
2005-03-15 | 3220.38 |  |  | 65.78
2005-03-14 | 3219.9 |  |  | 65.78
2005-03-13 | 3219.31 |  |  | 65.29
2005-03-12 | 3218.58 |  |  | 64.94
2005-03-11 | 3217.87 |  |  | 64.7
2005-03-10 | 3217.24 |  |  | 64.7
2005-03-09 | 3216.68 |  |  | 64.7
2005-03-08 | 3216.21 |  |  | 64.7
2005-03-07 | 3215.79 |  |  | 64.7
2005-03-06 | 3215.51 |  |  | 64.7
2005-03-05 | 3215.26 |  |  | 64.7
2005-03-04 | 3215.06 |  |  | 64.6
2005-03-03 | 3214.88 |  |  | 64.51
2005-03-02 | 3214.7 |  |  | 64.01
2005-03-01 | 3214.56 |  |  | 63.88
2005-02-28 | 3214.46 |  |  | 63.76
2005-02-27 | 3214.36 |  |  | 63.77
2005-02-26 | 3214.29 |  |  | 63.63
2005-02-25 | 3214.22 |  |  | 63.63
2005-02-24 | 3214.15 |  |  | 63.63
2005-02-23 | 3214.09 |  |  | 63.63
2005-02-22 | 3214.03 |  |  | 63.63
2005-02-21 | 3213.96 |  |  | 63.63
2005-02-20 | 3213.92 |  |  | 63.69
2005-02-19 | 3213.86 |  |  | 63.63
2005-02-18 | 3213.82 |  |  | 63.63
2005-02-17 | 3213.79 |  |  | 63.63
2005-02-16 | 3213.78 |  |  | 63.63
2005-02-15 | 3213.67 |  |  | 64.89
2005-02-14 | 3213.65 |  |  | 66.33
2005-02-13 | 3213.61 |  |  | 66.87
2005-02-12 | 3213.56 |  |  | 66.87
2005-02-11 | 3213.52 |  |  | 66.87
2005-02-10 | 3213.47 |  |  | 66.87
2005-02-09 | 3213.43 |  |  | 66.87
2005-02-08 | 3213.39 |  |  | 66.87
2005-02-07 | 3213.33 |  |  | 66.87
2005-02-06 | 3213.06 |  |  | 66.87
2005-02-05 | 3213.06 |  |  | 66.87
2005-02-04 | 3213.06 |  |  | 66.87
2005-02-03 | 3213.03 |  |  | 74.67
2005-02-02 | 3212.95 |  |  | 91.58
2005-02-01 | 3212.88 |  |  | 90.9
2005-01-31 | 3212.79 |  |  | 90.9
2005-01-30 | 3212.68 |  |  | 90.9
2005-01-29 | 3212.49 |  |  | 90.9
2005-01-28 | 3212.36 |  |  | 90.9
2005-01-27 | 3212.26 |  |  | 90.9
2005-01-26 | 3212.2 |  |  | 90.9
2005-01-25 | 3212.15 |  |  | 90.9
2005-01-24 | 3212.09 |  |  | 90.84
2005-01-23 | 3212.01 |  |  | 90.86
2005-01-22 | 3211.92 |  |  | 90.86
2005-01-21 | 3211.82 |  |  | 90.86
2005-01-20 | 3211.7 |  |  | 90.87
2005-01-19 | 3211.64 |  |  | 90.76
2005-01-18 | 3211.59 |  |  | 90.42
2005-01-17 | 3211.57 |  |  | 90.13
2005-01-16 | 3211.57 |  |  | 90.09
2005-01-15 | 3211.57 |  |  | 90.3
2005-01-14 | 3211.59 |  |  | 90.24
2005-01-13 | 3211.64 |  |  | 89.93
2005-01-12 | 3211.65 |  |  | 89.77
2005-01-11 | 3211.67 |  |  | 90.49
2005-01-10 | 3211.67 |  |  | 90.67
2005-01-09 | 3211.69 |  |  | 90.28
2005-01-08 | 3211.7 |  |  | 90.34
2005-01-07 | 3211.7 |  |  | 90.37
2005-01-06 | 3211.73 |  |  | 90.4
2005-01-05 | 3211.77 |  |  | 90.67
2005-01-04 | 3211.79 |  |  | 90.86
2005-01-03 | 3211.79 |  |  | 90.9
2005-01-02 | 3211.79 |  |  | 90.88
2005-01-01 | 3211.78 |  |  | 90.9
2004-12-31 | 3211.77 |  |  | 90.87
2004-12-30 | 3211.77 |  |  | 90.87
2004-12-29 | 3211.77 |  |  | 90.9
2004-12-28 | 3211.71 |  |  | 90.9
2004-12-27 | 3211.73 |  |  | 90.89
2004-12-26 | 3211.74 |  |  | 90.8
2004-12-25 | 3211.75 |  |  | 90.79
2004-12-24 | 3211.77 |  |  | 90.89
2004-12-23 | 3211.8 |  |  | 90.9
2004-12-22 | 3211.81 |  |  | 90.9
2004-12-21 | 3211.81 |  |  | 92.12
2004-12-20 | 3211.81 |  |  | 94.77
2004-12-19 | 3211.81 |  |  | 93.97
2004-12-18 | 3211.8 |  |  | 93.92
2004-12-17 | 3211.77 |  |  | 93.69
2004-12-16 | 3211.7 |  |  | 93.75
2004-12-15 | 3211.63 |  |  | 93.55
2004-12-14 | 3211.56 |  |  | 93.62
2004-12-13 | 3211.47 |  |  | 93.64
2004-12-12 | 3211.39 |  |  | 93.59
2004-12-11 | 3211.35 |  |  | 93.62
2004-12-10 | 3211.29 |  |  | 93.59
2004-12-09 | 3211.29 |  |  | 93.64
2004-12-08 | 3211.26 |  |  | 93.98
2004-12-07 | 3211.21 |  |  | 93.67
2004-12-06 | 3211.27 |  |  | 93.75
2004-12-05 | 3211.29 |  |  | 93.53
2004-12-04 | 3211.33 |  |  | 93.55
2004-12-03 | 3211.38 |  |  | 93.57
2004-12-02 | 3211.39 |  |  | 93.53
2004-12-01 | 3211.42 |  |  | 93.53
2004-11-30 | 3211.42 |  |  | 93.53
2004-11-29 | 3211.46 |  |  | 93.53
2004-11-28 | 3211.49 |  |  | 93.53
2004-11-27 | 3211.52 |  |  | 93.53
2004-11-26 | 3211.55 |  |  | 93.53
2004-11-25 | 3211.6 |  |  | 93.53
2004-11-24 | 3211.62 |  |  | 93.53
2004-11-23 | 3211.64 |  |  | 93.53
2004-11-22 | 3211.67 |  |  | 93.53
2004-11-21 | 3211.72 |  |  | 93.53
2004-11-20 | 3211.76 |  |  | 93.53
2004-11-19 | 3211.79 |  |  | 93.53
2004-11-18 | 3211.81 |  |  | 93.53
2004-11-17 | 3211.86 |  |  | 93.53
2004-11-16 | 3211.89 |  |  | 93.53
2004-11-15 | 3211.91 |  |  | 93.53
2004-11-14 | 3211.94 |  |  | 93.53
2004-11-13 | 3211.96 |  |  | 93.53
2004-11-12 | 3211.99 |  |  | 93.53
2004-11-11 | 3212.03 |  |  | 93.53
2004-11-10 | 3212.06 |  |  | 93.55
2004-11-09 | 3212.06 |  |  | 93.53
2004-11-08 | 3212.11 |  |  | 105.37
2004-11-07 | 3212.14 |  |  | 124.48
2004-11-06 | 3212.19 |  |  | 124.39
2004-11-05 | 3212.26 |  |  | 133.36
2004-11-04 | 3212.3 |  |  | 150.08
2004-11-03 | 3212.39 |  |  | 150.08
2004-11-02 | 3212.49 |  |  | 149.02
2004-11-01 | 3212.58 |  |  | 148.35
2004-10-31 | 3212.67 |  |  | 132.98
2004-10-30 | 3212.75 |  |  | 125.68
2004-10-29 | 3212.85 |  |  | 126.33
2004-10-28 | 3212.88 |  |  | 126.89
2004-10-27 | 3212.93 |  |  | 126.91
2004-10-26 | 3212.99 |  |  | 126.88
2004-10-25 | 3213 |  |  | 126.91
2004-10-24 | 3213.08 |  |  | 126.91
2004-10-23 | 3213.13 |  |  | 126.1
2004-10-22 | 3213.17 |  |  | 125.34
2004-10-21 | 3213.23 |  |  | 114.27
2004-10-20 | 3213.28 |  |  | 94.86
2004-10-19 | 3213.3 |  |  | 93.01
2004-10-18 | 3213.33 |  |  | 80.63
2004-10-17 | 3213.38 |  |  | 67.98
2004-10-16 | 3213.43 |  |  | 67.98
2004-10-15 | 3213.46 |  |  | 77.49
2004-10-14 | 3213.5 |  |  | 103.31
2004-10-13 | 3213.55 |  |  | 120.69
2004-10-12 | 3213.63 |  |  | 131.04
2004-10-11 | 3213.73 |  |  | 144.93
2004-10-10 | 3213.85 |  |  | 144.93
2004-10-09 | 3213.98 |  |  | 144.93
2004-10-08 | 3214.12 |  |  | 144.93
2004-10-07 | 3214.26 |  |  | 144.93
2004-10-06 | 3214.38 |  |  | 145.03
2004-10-05 | 3214.51 |  |  | 148.4
2004-10-04 | 3214.63 |  |  | 160.31
2004-10-03 | 3214.76 |  |  | 160.53
2004-10-02 | 3214.89 |  |  | 160.68
2004-10-01 | 3215.02 |  |  | 160.68
2004-09-30 | 3215.15 |  |  | 166.17
2004-09-29 | 3215.31 |  |  | 175.46
2004-09-28 | 3215.49 |  |  | 175.46
2004-09-27 | 3215.63 |  |  | 175.46
2004-09-26 | 3215.76 |  |  | 175.46
2004-09-25 | 3215.91 |  |  | 175.46
2004-09-24 | 3216.05 |  |  | 182.83
2004-09-23 | 3216.21 |  |  | 196.16
2004-09-22 | 3216.35 |  |  | 196.16
2004-09-21 | 3216.49 |  |  | 196.16
2004-09-20 | 3216.65 |  |  | 201.29
2004-09-19 | 3216.83 |  |  | 209.07
2004-09-18 | 3217.01 |  |  | 210.14
2004-09-17 | 3217.22 |  |  | 216
2004-09-16 | 3217.41 |  |  | 222.32
2004-09-15 | 3217.62 |  |  | 222.32
2004-09-14 | 3217.81 |  |  | 222.32
2004-09-13 | 3218.01 |  |  | 227.98
2004-09-12 | 3218.22 |  |  | 236.23
2004-09-11 | 3218.44 |  |  | 236.06
2004-09-10 | 3218.65 |  |  | 236.26
2004-09-09 | 3218.85 |  |  | 236.07
2004-09-08 | 3219.06 |  |  | 236.19
2004-09-07 | 3219.27 |  |  | 236.26
2004-09-06 | 3219.47 |  |  | 236.46
2004-09-05 | 3219.67 |  |  | 236.46
2004-09-04 | 3219.89 |  |  | 236.46
2004-09-03 | 3220.1 |  |  | 236.46
2004-09-02 | 3220.29 |  |  | 236.46
2004-09-01 | 3220.53 |  |  | 236.46
2004-08-31 | 3220.73 |  |  | 236.46
2004-08-30 | 3220.94 |  |  | 236.46
2004-08-29 | 3221.16 |  |  | 236.46
2004-08-28 | 3221.35 |  |  | 236.46
2004-08-27 | 3221.53 |  |  | 236.46
2004-08-26 | 3221.71 |  |  | 236.46
2004-08-25 | 3221.93 |  |  | 236.48
2004-08-24 | 3222.15 |  |  | 236.5
2004-08-23 | 3222.35 |  |  | 236.48
2004-08-22 | 3222.53 |  |  | 236.7
2004-08-21 | 3222.75 |  |  | 236.78
2004-08-20 | 3222.99 |  |  | 236.74
2004-08-19 | 3223.17 |  |  | 236.72
2004-08-18 | 3223.38 |  |  | 236.81
2004-08-17 | 3223.56 |  |  | 237.02
2004-08-16 | 3223.74 |  |  | 237.29
2004-08-15 | 3223.92 |  |  | 238.05
2004-08-14 | 3224.11 |  |  | 238.26
2004-08-13 | 3224.31 |  |  | 237.84
2004-08-12 | 3224.51 |  |  | 234.77
2004-08-11 | 3224.69 |  |  | 238.56
2004-08-10 | 3224.89 |  |  | 236.96
2004-08-09 | 3225.07 |  |  | 226.2
2004-08-08 | 3225.2 |  |  | 226.18
2004-08-07 | 3225.38 |  |  | 226.2
2004-08-06 | 3225.58 |  |  | 226.22
2004-08-05 | 3225.78 |  |  | 226.31
2004-08-04 | 3226 |  |  | 226.26
2004-08-03 | 3226.21 |  |  | 226.73
2004-08-02 | 3226.43 |  |  | 226.88
2004-08-01 | 3226.64 |  |  | 226.94
2004-07-31 | 3226.82 |  |  | 226.96
2004-07-30 | 3227.02 |  |  | 227.18
2004-07-29 | 3227.23 |  |  | 227.43
2004-07-28 | 3227.46 |  |  | 227.9
2004-07-27 | 3227.65 |  |  | 228.19
2004-07-26 | 3227.84 |  |  | 228.23
2004-07-25 | 3228.03 |  |  | 228.23
2004-07-24 | 3228.22 |  |  | 228.23
2004-07-23 | 3228.38 |  |  | 228.23
2004-07-22 | 3228.57 |  |  | 228.23
2004-07-21 | 3228.74 |  |  | 228.25
2004-07-20 | 3228.94 |  |  | 228.3
2004-07-19 | 3229.1 |  |  | 228.51
2004-07-18 | 3229.26 |  |  | 228.49
2004-07-17 | 3229.44 |  |  | 228.61
2004-07-16 | 3229.62 |  |  | 224.75
2004-07-15 | 3229.79 |  |  | 216.6
2004-07-14 | 3229.96 |  |  | 216.58
2004-07-13 | 3230.12 |  |  | 216.58
2004-07-12 | 3230.28 |  |  | 216.6
2004-07-11 | 3230.4 |  |  | 216.58
2004-07-10 | 3230.56 |  |  | 216.78
2004-07-09 | 3230.74 |  |  | 216.93
2004-07-08 | 3230.9 |  |  | 216.58
2004-07-07 | 3231.08 |  |  | 216.66
2004-07-06 | 3231.27 |  |  | 216.91
2004-07-05 | 3231.42 |  |  | 216.84
2004-07-04 | 3231.55 |  |  | 217.17
2004-07-03 | 3231.74 |  |  | 217.17
2004-07-02 | 3231.87 |  |  | 217.21
2004-07-01 | 3232.02 |  |  | 232.92
2004-06-30 | 3232.14 |  |  | 247.43
2004-06-29 | 3232.3 |  |  | 247.41
2004-06-28 | 3232.45 |  |  | 247.29
2004-06-27 | 3232.58 |  |  | 247.27
2004-06-26 | 3232.74 |  |  | 247.09
2004-06-25 | 3232.91 |  |  | 246.98
2004-06-24 | 3233.07 |  |  | 246.96
2004-06-23 | 3233.2 |  |  | 246.96
2004-06-22 | 3233.33 |  |  | 246.51
2004-06-21 | 3233.45 |  |  | 245.98
2004-06-20 | 3233.57 |  |  | 245.19
2004-06-19 | 3233.68 |  |  | 244.84
2004-06-18 | 3233.83 |  |  | 244.84
2004-06-17 | 3233.96 |  |  | 244.84
2004-06-16 | 3234.06 |  |  | 244.84
2004-06-15 | 3234.18 |  |  | 249.67
2004-06-14 | 3234.25 |  |  | 253.4
2004-06-13 | 3234.38 |  |  | 253.38
2004-06-12 | 3234.43 |  |  | 253.38
2004-06-11 | 3234.5 |  |  | 253.36
2004-06-10 | 3234.56 |  |  | 253.36
2004-06-09 | 3234.59 |  |  | 252.88
2004-06-08 | 3234.63 |  |  | 252.63
2004-06-07 | 3234.69 |  |  | 252.35
2004-06-06 | 3234.78 |  |  | 252.19
2004-06-05 | 3234.87 |  |  | 252.26
2004-06-04 | 3234.94 |  |  | 251.39
2004-06-03 | 3234.98 |  |  | 278.4
2004-06-02 | 3235.02 |  |  | 345.74
2004-06-01 | 3235.08 |  |  | 462.69
2004-05-31 | 3235.16 |  |  | 614.62
2004-05-30 | 3235.29 |  |  | 704.86
2004-05-29 | 3235.44 |  |  | 713.03
2004-05-28 | 3235.53 |  |  | 723.32
2004-05-27 | 3235.68 |  |  | 736.65
2004-05-26 | 3235.89 |  |  | 688.23
2004-05-25 | 3235.99 |  |  | 581.74
2004-05-24 | 3235.95 |  |  | 492.88
2004-05-23 | 3235.82 |  |  | 481.35
2004-05-22 | 3235.7 |  |  | 467.51
2004-05-21 | 3235.52 |  |  | 448.84
2004-05-20 | 3235.21 |  |  | 431.75
2004-05-19 | 3234.88 |  |  | 395.6
2004-05-18 | 3234.57 |  |  | 270.43
2004-05-17 | 3234.6 |  |  | 252.84
2004-05-16 | 3234.66 |  |  | 252.66
2004-05-15 | 3234.73 |  |  | 252.46
2004-05-14 | 3234.83 |  |  | 252.38
2004-05-13 | 3234.88 |  |  | 258.72
2004-05-12 | 3234.93 |  |  | 266.43
2004-05-11 | 3234.96 |  |  | 268.7
2004-05-10 | 3234.98 |  |  | 268.7
2004-05-09 | 3235.03 |  |  | 268.7
2004-05-08 | 3235.06 |  |  | 268.87
2004-05-07 | 3235.08 |  |  | 271.57
2004-05-06 | 3235.08 |  |  | 300.72
2004-05-05 | 3235.1 |  |  | 342.6
2004-05-04 | 3235.16 |  |  | 439.11
2004-05-03 | 3235.24 |  |  | 573
2004-05-02 | 3235.38 |  |  | 641.43
2004-05-01 | 3235.52 |  |  | 652.47
2004-04-30 | 3235.65 |  |  | 663.26
2004-04-29 | 3235.75 |  |  | 673.8
2004-04-28 | 3235.84 |  |  | 683.01
2004-04-27 | 3235.97 |  |  | 695.07
2004-04-26 | 3236.07 |  |  | 702.41
2004-04-25 | 3236.08 |  |  | 706.52
2004-04-24 | 3236.06 |  |  | 703.03
2004-04-23 | 3236.01 |  |  | 694.48
2004-04-22 | 3235.88 |  |  | 674.15
2004-04-21 | 3235.62 |  |  | 651.53
2004-04-20 | 3235.42 |  |  | 642.25
2004-04-19 | 3235.42 |  |  | 642.76
2004-04-18 | 3235.42 |  |  | 640.51
2004-04-17 | 3235.36 |  |  | 628.68
2004-04-16 | 3235.21 |  |  | 613.96
2004-04-15 | 3235.01 |  |  | 611.63
2004-04-14 | 3234.9 |  |  | 610.7
2004-04-13 | 3234.85 |  |  | 609.49
2004-04-12 | 3234.78 |  |  | 605.71
2004-04-11 | 3234.66 |  |  | 699.83
2004-04-10 | 3234.58 |  |  | 822.23
2004-04-09 | 3234.51 |  |  | 964.59
2004-04-08 | 3234.46 |  |  | 1078.64
2004-04-07 | 3234.5 |  |  | 1077.95
2004-04-06 | 3234.36 |  |  | 1076.74
2004-04-05 | 3234.24 |  |  | 955.6
2004-04-04 | 3234.07 |  |  | 846.84
2004-04-03 | 3233.9 |  |  | 846.84
2004-04-02 | 3233.8 |  |  | 846.84
2004-04-01 | 3233.68 |  |  | 951.38
2004-03-31 | 3233.47 |  |  | 1072.96
2004-03-30 | 3233.14 |  |  | 1222.25
2004-03-29 | 3233 |  |  | 1302.95
2004-03-28 | 3232.99 |  |  | 1366.85
2004-03-27 | 3232.9 |  |  | 1412.75
2004-03-26 | 3232.75 |  |  | 1541.68
2004-03-25 | 3232.53 |  |  | 1626.53
2004-03-24 | 3232.15 |  |  | 1621.61
2004-03-23 | 3231.34 |  |  | 1616.62
2004-03-22 | 3230.42 |  |  | 1822.67
2004-03-21 | 3229.74 |  |  | 2050.15
2004-03-20 | 3229.53 |  |  | 2049.67
2004-03-19 | 3229.08 |  |  | 2044.81
2004-03-18 | 3228.1 |  |  | 2041.48
2004-03-17 | 3227.62 |  |  | 2037.47
2004-03-16 | 3227.27 |  |  | 2038.26
2004-03-15 | 3227.06 |  |  | 1524.26
2004-03-14 | 3226.38 |  |  | 1161
2004-03-13 | 3225.72 |  |  | 773.27
2004-03-12 | 3224.84 |  |  | 512.76
2004-03-11 | 3224.04 |  |  | 475.98
2004-03-10 | 3223.2 |  |  | 416.03
2004-03-09 | 3222.3 |  |  | 211.85
2004-03-08 | 3221.4 |  |  | 194.36
2004-03-07 | 3220.99 |  |  | 194.36
2004-03-06 | 3220.79 |  |  | 194.36
2004-03-05 | 3220.58 |  |  | 194.36
2004-03-04 | 3220.39 |  |  | 193.43
2004-03-03 | 3220.14 |  |  | 192.57
2004-03-02 | 3219.85 |  |  | 192.57
2004-03-01 | 3219.51 |  |  | 182.39
2004-02-29 | 3219.25 |  |  | 164.31
2004-02-28 | 3218.88 |  |  | 164.31
2004-02-27 | 3218.49 |  |  | 153.83
2004-02-26 | 3218.13 |  |  | 122.33
2004-02-25 | 3217.78 |  |  | 104.85
2004-02-24 | 3217.37 |  |  | 104.49
2004-02-23 | 3216.96 |  |  | 104.49
2004-02-22 | 3216.49 |  |  | 104.49
2004-02-21 | 3215.98 |  |  | 103.77
2004-02-20 | 3215.32 |  |  | 103.1
2004-02-19 | 3214.22 |  |  | 103.08
2004-02-18 | 3212.96 |  |  | 103.05
2004-02-17 | 3211.66 |  |  | 102.84
2004-02-16 | 3211.25 |  |  | 102.38
2004-02-15 | 3211.13 |  |  | 102.01
2004-02-14 | 3211.03 |  |  | 101.93
2004-02-13 | 3210.95 |  |  | 101.88
2004-02-12 | 3210.92 |  |  | 102.11
2004-02-11 | 3210.85 |  |  | 100.76
2004-02-10 | 3210.78 |  |  | 95.14
2004-02-09 | 3210.71 |  |  | 94.89
2004-02-08 | 3210.58 |  |  | 94.86
2004-02-07 | 3210.46 |  |  | 94.86
2004-02-06 | 3210.31 |  |  | 87.77
2004-02-05 | 3210.22 |  |  | 74.82
2004-02-04 | 3210.02 |  |  | 74.81
2004-02-03 | 3209.82 |  |  | 74.83
2004-02-02 | 3209.49 |  |  | 74.85
2004-02-01 | 3209.16 |  |  | 74.81
2004-01-31 | 3208.86 |  |  | 74.81
2004-01-30 | 3208.37 |  |  | 74.79
2004-01-29 | 3208.05 |  |  | 74.7
2004-01-28 | 3207.94 |  |  | 74.28
2004-01-27 | 3207.83 |  |  | 74.08
2004-01-26 | 3207.66 |  |  | 73.77
2004-01-25 | 3207.57 |  |  | 73.71
2004-01-24 | 3207.5 |  |  | 73.96
2004-01-23 | 3207.42 |  |  | 73.92
2004-01-22 | 3207.37 |  |  | 73.74
2004-01-21 | 3207.3 |  |  | 73.85
2004-01-20 | 3207.2 |  |  | 73.66
2004-01-19 | 3207.13 |  |  | 74.13
2004-01-18 | 3207.03 |  |  | 74.8
2004-01-17 | 3206.97 |  |  | 74.71
2004-01-16 | 3206.88 |  |  | 74.75
2004-01-15 | 3206.77 |  |  | 74.4
2004-01-14 | 3206.64 |  |  | 73.98
2004-01-13 | 3206.46 |  |  | 73.69
2004-01-12 | 3206.27 |  |  | 73.65
2004-01-11 | 3206.13 |  |  | 73.65
2004-01-10 | 3206.11 |  |  | 73.65
2004-01-09 | 3206.1 |  |  | 73.66
2004-01-08 | 3206.1 |  |  | 73.66
2004-01-07 | 3206.1 |  |  | 73.65
2004-01-06 | 3206.12 |  |  | 73.65
2004-01-05 | 3206.14 |  |  | 73.65
2004-01-04 | 3206.17 |  |  | 73.73
2004-01-03 | 3206.21 |  |  | 73.65
2004-01-02 | 3206.22 |  |  | 73.65
2004-01-01 | 3206.16 |  |  | 73.91
2003-12-31 | 3206.22 |  |  | 73.65
2003-12-30 | 3206.22 |  |  | 73.68
2003-12-29 | 3206.22 |  |  | 73.87
2003-12-28 | 3206.13 |  |  | 73.77
2003-12-27 | 3206.11 |  |  | 73.65
2003-12-26 | 3206.22 |  |  | 73.65
2003-12-25 | 3206.19 |  |  | 73.65
2003-12-24 | 3206.23 |  |  | 73.74
2003-12-23 | 3206.28 |  |  | 73.82
2003-12-22 | 3206.31 |  |  | 73.68
2003-12-21 | 3206.21 |  |  | 73.65
2003-12-20 | 3206.21 |  |  | 73.65
2003-12-19 | 3206.21 |  |  | 73.72
2003-12-18 | 3206.12 |  |  | 73.65
2003-12-17 | 3206.12 |  |  | 73.65
2003-12-16 | 3206.12 |  |  | 73.65
2003-12-15 | 3206.12 |  |  | 69.23
2003-12-14 | 3206 |  |  | 62.56
2003-12-13 | 3205.98 |  |  | 62.57
2003-12-12 | 3205.98 |  |  | 64.23
2003-12-11 | 3205.95 |  |  | 67.98
2003-12-10 | 3205.95 |  |  | 67.98
2003-12-09 | 3205.95 |  |  | 67.98
2003-12-08 | 3205.95 |  |  | 67.98
2003-12-07 | 3205.95 |  |  | 67.98
2003-12-06 | 3205.95 |  |  | 68
2003-12-05 | 3205.95 |  |  | 68
2003-12-04 | 3205.92 |  |  | 68
2003-12-03 | 3205.92 |  |  | 67.98
2003-12-02 | 3205.87 |  |  | 67.98
2003-12-01 | 3205.86 |  |  | 67.98
2003-11-30 | 3205.86 |  |  | 68
2003-11-29 | 3205.85 |  |  | 67.99
2003-11-28 | 3205.85 |  |  | 68.01
2003-11-27 | 3205.87 |  |  | 67.98
2003-11-26 | 3205.9 |  |  | 67.98
2003-11-25 | 3205.9 |  |  | 67.98
2003-11-24 | 3205.91 |  |  | 67.98
2003-11-23 | 3205.91 |  |  | 67.98
2003-11-22 | 3205.92 |  |  | 67.98
2003-11-21 | 3205.92 |  |  | 67.98
2003-11-20 | 3205.98 |  |  | 67.98
2003-11-19 | 3205.98 |  |  | 68.05
2003-11-18 | 3206 |  |  | 67.98
2003-11-17 | 3206.04 |  |  | 67.98
2003-11-16 | 3206.04 |  |  | 67.98
2003-11-15 | 3206.05 |  |  | 67.98
2003-11-14 | 3206.05 |  |  | 67.98
2003-11-13 | 3206.05 |  |  | 67.98
2003-11-12 | 3206.05 |  |  | 67.98
2003-11-11 | 3206.13 |  |  | 68.05
2003-11-10 | 3206.14 |  |  | 68
2003-11-09 | 3206.14 |  |  | 67.98
2003-11-08 | 3206.14 |  |  | 68.09
2003-11-07 | 3206.16 |  |  | 68.01
2003-11-06 | 3206.2 |  |  | 68
2003-11-05 | 3206.25 |  |  | 67.98
2003-11-04 | 3206.27 |  |  | 67.98
2003-11-03 | 3206.31 |  |  | 68.91
2003-11-02 | 3206.33 |  |  | 69.09
2003-11-01 | 3206.35 |  |  | 68.79
2003-10-31 | 3206.4 |  |  | 69.03
2003-10-30 | 3206.45 |  |  | 69.09
2003-10-29 | 3206.49 |  |  | 69.09
2003-10-28 | 3206.58 |  |  | 69.09
2003-10-27 | 3206.62 |  |  | 69.09
2003-10-26 | 3206.68 |  |  | 69.09
2003-10-25 | 3206.73 |  |  | 69.09
2003-10-24 | 3206.77 |  |  | 69.09
2003-10-23 | 3206.82 |  |  | 69.09
2003-10-22 | 3206.87 |  |  | 69.09
2003-10-21 | 3206.92 |  |  | 69.09
2003-10-20 | 3206.94 |  |  | 68.28
2003-10-19 | 3207 |  |  | 66.87
2003-10-18 | 3207.04 |  |  | 66.84
2003-10-17 | 3207.07 |  |  | 66.67
2003-10-16 | 3207.12 |  |  | 66.73
2003-10-15 | 3207.14 |  |  | 70.82
2003-10-14 | 3207.12 |  |  | 89.58
2003-10-13 | 3207.19 |  |  | 128.49
2003-10-12 | 3207.34 |  |  | 167.98
2003-10-11 | 3207.53 |  |  | 167.98
2003-10-10 | 3207.69 |  |  | 167.98
2003-10-09 | 3207.86 |  |  | 167.98
2003-10-08 | 3208.09 |  |  | 167.98
2003-10-07 | 3208.28 |  |  | 167.98
2003-10-06 | 3208.47 |  |  | 167.98
2003-10-05 | 3208.64 |  |  | 167.98
2003-10-04 | 3208.79 |  |  | 167.98
2003-10-03 | 3208.96 |  |  | 167.98
2003-10-02 | 3209.14 |  |  | 167.98
2003-10-01 | 3209.27 |  |  | 167.98
2003-09-30 | 3209.5 |  |  | 170
2003-09-29 | 3209.66 |  |  | 170
2003-09-28 | 3209.84 |  |  | 170
2003-09-27 | 3209.99 |  |  | 170
2003-09-26 | 3210.16 |  |  | 171
2003-09-25 | 3210.34 |  |  | 172
2003-09-24 | 3210.52 |  |  | 172
2003-09-23 | 3210.68 |  |  | 172
2003-09-22 | 3210.87 |  |  | 172
2003-09-21 | 3211.02 |  |  | 172
2003-09-20 | 3211.21 |  |  | 172
2003-09-19 | 3211.36 |  |  | 172
2003-09-18 | 3211.51 |  |  | 172
2003-09-17 | 3211.72 |  |  | 174
2003-09-16 | 3211.88 |  |  | 177
2003-09-15 | 3212.09 |  |  | 177
2003-09-14 | 3212.27 |  |  | 177
2003-09-13 | 3212.42 |  |  | 177
2003-09-12 | 3212.61 |  |  | 177
2003-09-11 | 3212.79 |  |  | 177
2003-09-10 | 3212.99 |  |  | 184
2003-09-09 | 3213.18 |  |  | 203
2003-09-08 | 3213.35 |  |  | 218
2003-09-07 | 3213.6 |  |  | 218
2003-09-06 | 3213.85 |  |  | 218
2003-09-05 | 3214.06 |  |  | 218
2003-09-04 | 3214.3 |  |  | 218
2003-09-03 | 3214.51 |  |  | 218
2003-09-02 | 3214.67 |  |  | 218
2003-09-01 | 3215.06 |  |  | 218
2003-08-31 | 3215.1 |  |  | 218
2003-08-30 | 3215.28 |  |  | 217
2003-08-29 | 3215.48 |  |  | 219
2003-08-28 | 3215.72 |  |  | 222
2003-08-27 | 3215.95 |  |  | 222
2003-08-26 | 3216.13 |  |  | 222
2003-08-25 | 3216.46 |  |  | 222
2003-08-24 | 3216.6 |  |  | 222
2003-08-23 | 3216.82 |  |  | 223
2003-08-22 | 3217.05 |  |  | 224
2003-08-21 | 3217.27 |  |  | 224
2003-08-20 | 3217.5 |  |  | 224
2003-08-19 | 3217.73 |  |  | 224
2003-08-18 | 3217.89 |  |  | 224
2003-08-17 | 3218.09 |  |  | 224
2003-08-16 | 3218.31 |  |  | 224
2003-08-15 | 3218.53 |  |  | 224
2003-08-14 | 3218.75 |  |  | 224
2003-08-13 | 3218.94 |  |  | 224
2003-08-12 | 3219.15 |  |  | 224
2003-08-11 | 3219.37 |  |  | 224
2003-08-10 | 3219.62 |  |  | 224
2003-08-09 | 3219.88 |  |  | 224
2003-08-08 | 3220.05 |  |  | 224
2003-08-07 | 3220.25 |  |  | 224
2003-08-06 | 3220.46 |  |  | 224
2003-08-05 | 3220.67 |  |  | 224
2003-08-04 | 3220.88 |  |  | 225
2003-08-03 | 3221.08 |  |  | 226
2003-08-02 | 3221.27 |  |  | 226
2003-08-01 | 3221.5 |  |  | 226
2003-07-31 | 3221.72 |  |  | 226
2003-07-30 | 3221.98 |  |  | 226
2003-07-29 | 3222.18 |  |  | 226
2003-07-28 | 3222.36 |  |  | 226
2003-07-27 | 3222.57 |  |  | 226
2003-07-26 | 3222.77 |  |  | 226
2003-07-25 | 3222.98 |  |  | 226
2003-07-24 | 3223.24 |  |  | 226
2003-07-23 | 3223.46 |  |  | 226
2003-07-22 | 3223.68 |  |  | 226
2003-07-21 | 3223.87 |  |  | 226
2003-07-20 | 3224.07 |  |  | 226
2003-07-19 | 3224.23 |  |  | 226
2003-07-18 | 3224.38 |  |  | 226
2003-07-17 | 3224.55 |  |  | 226
2003-07-16 | 3224.75 |  |  | 226
2003-07-15 | 3224.92 |  |  | 226
2003-07-14 | 3225.11 |  |  | 226
2003-07-13 | 3225.28 |  |  | 227
2003-07-12 | 3225.49 |  |  | 228
2003-07-11 | 3225.72 |  |  | 228
2003-07-10 | 3225.89 |  |  | 225
2003-07-09 | 3226.12 |  |  | 221
2003-07-08 | 3226.31 |  |  | 222
2003-07-07 | 3226.5 |  |  | 222
2003-07-06 | 3226.67 |  |  | 222
2003-07-05 | 3226.85 |  |  | 222
2003-07-04 | 3227.02 |  |  | 222
2003-07-03 | 3227.19 |  |  | 222
2003-07-02 | 3227.36 |  |  | 222
2003-07-01 | 3227.49 |  |  | 222
2003-06-30 | 3227.7 |  |  | 222
2003-06-29 | 3227.94 |  |  | 222
2003-06-28 | 3228.1 |  |  | 222
2003-06-27 | 3228.27 |  |  | 222
2003-06-26 | 3228.45 |  |  | 222
2003-06-25 | 3228.59 |  |  | 222
2003-06-24 | 3228.76 |  |  | 222
2003-06-23 | 3228.93 |  |  | 222
2003-06-22 | 3229.14 |  |  | 222
2003-06-21 | 3229.31 |  |  | 223
2003-06-20 | 3229.55 |  |  | 224
2003-06-19 | 3229.7 |  |  | 225
2003-06-18 | 3229.94 |  |  | 226
2003-06-17 | 3230.07 |  |  | 226
2003-06-16 | 3230.27 |  |  | 226
2003-06-15 | 3230.4 |  |  | 226
2003-06-14 | 3230.58 |  |  | 226
2003-06-13 | 3230.76 |  |  | 226
2003-06-12 | 3230.94 |  |  | 226
2003-06-11 | 3231.14 |  |  | 226
2003-06-10 | 3231.31 |  |  | 226
2003-06-09 | 3231.47 |  |  | 226
2003-06-08 | 3231.69 |  |  | 226
2003-06-07 | 3231.87 |  |  | 226
2003-06-06 | 3231.98 |  |  | 226
2003-06-05 | 3232.14 |  |  | 226
2003-06-04 | 3232.24 |  |  | 226
2003-06-03 | 3232.4 |  |  | 226
2003-06-02 | 3232.47 |  |  | 226
2003-06-01 | 3232.55 |  |  | 226
2003-05-31 | 3232.56 |  |  | 226
2003-05-30 | 3232.7 |  |  | 226
2003-05-29 | 3232.79 |  |  | 226
2003-05-28 | 3232.91 |  |  | 226
2003-05-27 | 3232.99 |  |  | 226
2003-05-26 | 3233.06 |  |  | 226
2003-05-25 | 3233.12 |  |  | 227
2003-05-24 | 3233.2 |  |  | 227
2003-05-23 | 3233.27 |  |  | 226
2003-05-22 | 3233.33 |  |  | 226
2003-05-21 | 3233.39 |  |  | 226
2003-05-20 | 3233.4 |  |  | 226
2003-05-19 | 3233.4 |  |  | 222
2003-05-18 | 3233.43 |  |  | 215
2003-05-17 | 3233.43 |  |  | 215
2003-05-16 | 3233.43 |  |  | 215
2003-05-15 | 3233.43 |  |  | 212
2003-05-14 | 3233.4 |  |  | 211
2003-05-13 | 3233.31 |  |  | 204
2003-05-12 | 3233.13 |  |  | 189
2003-05-11 | 3232.87 |  |  | 189
2003-05-10 | 3232.81 |  |  | 189
2003-05-09 | 3232.78 |  |  | 189
2003-05-08 | 3232.74 |  |  | 189
2003-05-07 | 3232.7 |  |  | 175
2003-05-06 | 3232.56 |  |  | 143
2003-05-05 | 3232.4 |  |  | 143
2003-05-04 | 3232.26 |  |  | 143
2003-05-03 | 3232.14 |  |  | 143
2003-05-02 | 3232.02 |  |  | 135
2003-05-01 | 3231.88 |  |  | 116
2003-04-30 | 3231.7 |  |  | 116
2003-04-29 | 3231.46 |  |  | 115
2003-04-28 | 3231.23 |  |  | 115
2003-04-27 | 3231.07 |  |  | 115
2003-04-26 | 3230.86 |  |  | 115
2003-04-25 | 3230.67 |  |  | 115
2003-04-24 | 3230.5 |  |  | 127
2003-04-23 | 3230.37 |  |  | 138
2003-04-22 | 3230.27 |  |  | 138
2003-04-21 | 3230.24 |  |  | 138
2003-04-20 | 3230.14 |  |  | 138
2003-04-19 | 3230.06 |  |  | 138
2003-04-18 | 3229.87 |  |  | 138
2003-04-17 | 3229.79 |  |  | 138
2003-04-16 | 3229.66 |  |  | 138
2003-04-15 | 3229.44 |  |  | 138
2003-04-14 | 3229.26 |  |  | 138
2003-04-13 | 3229.1 |  |  | 133
2003-04-12 | 3228.91 |  |  | 108
2003-04-11 | 3228.68 |  |  | 79
2003-04-10 | 3228.41 |  |  | 71
2003-04-09 | 3228.14 |  |  | 70
2003-04-08 | 3227.81 |  |  | 71
2003-04-07 | 3227.53 |  |  | 70
2003-04-06 | 3227.21 |  |  | 70
2003-04-05 | 3226.96 |  |  | 70
2003-04-04 | 3226.69 |  |  | 70
2003-04-03 | 3226.39 |  |  | 70
2003-04-02 | 3226.1 |  |  | 70
2003-04-01 | 3225.68 |  |  | 70
2003-03-31 | 3225.27 |  |  | 69
2003-03-30 | 3224.92 |  |  | 69
2003-03-29 | 3224.58 |  |  | 69
2003-03-28 | 3224.11 |  |  | 69
2003-03-27 | 3223.6 |  |  | 69
2003-03-26 | 3222.91 |  |  | 69
2003-03-25 | 3222.26 |  |  | 69
2003-03-24 | 3221.83 |  |  | 69
2003-03-23 | 3221.3 |  |  | 69
2003-03-22 | 3220.66 |  |  | 68
2003-03-21 | 3220.32 |  |  | 68
2003-03-20 | 3220.02 |  |  | 68
2003-03-19 | 3219.71 |  |  | 68
2003-03-18 | 3219.34 |  |  | 68
2003-03-17 | 3218.82 |  |  | 68
2003-03-16 | 3218.11 |  |  | 68
2003-03-15 | 3217.2 |  |  | 67
2003-03-14 | 3216.39 |  |  | 67
2003-03-13 | 3215.75 |  |  | 67
2003-03-12 | 3215.44 |  |  | 67
2003-03-11 | 3215.11 |  |  | 67
2003-03-10 | 3214.86 |  |  | 66
2003-03-09 | 3214.8 |  |  | 66
2003-03-08 | 3214.74 |  |  | 66
2003-03-07 | 3214.68 |  |  | 66
2003-03-06 | 3214.63 |  |  | 66
2003-03-05 | 3214.59 |  |  | 66
2003-03-04 | 3214.55 |  |  | 66
2003-03-03 | 3214.5 |  |  | 66
2003-03-02 | 3214.45 |  |  | 66
2003-03-01 | 3214.4 |  |  | 66
2003-02-28 | 3214.35 |  |  | 66
2003-02-27 | 3214.32 |  |  | 66
2003-02-26 | 3214.26 |  |  | 66
2003-02-25 | 3214.2 |  |  | 66
2003-02-24 | 3214.1 |  |  | 66
2003-02-23 | 3214 |  |  | 66
2003-02-22 | 3213.86 |  |  | 66
2003-02-21 | 3213.74 |  |  | 66
2003-02-20 | 3213.6 |  |  | 66
2003-02-19 | 3213.46 |  |  | 66
2003-02-18 | 3213.3 |  |  | 66
2003-02-17 | 3213.08 |  |  | 66
2003-02-16 | 3212.9 |  |  | 66
2003-02-15 | 3212.76 |  |  | 65
2003-02-14 | 3212.62 |  |  | 65
2003-02-13 | 3212.5 |  |  | 65
2003-02-12 | 3212.38 |  |  | 65
2003-02-11 | 3212.29 |  |  | 65
2003-02-10 | 3212.19 |  |  | 65
2003-02-09 | 3212.07 |  |  | 65
2003-02-08 | 3211.92 |  |  | 65
2003-02-07 | 3211.77 |  |  | 66
2003-02-06 | 3211.56 |  |  | 66
2003-02-05 | 3211.37 |  |  | 66
2003-02-04 | 3211.02 |  |  | 66
2003-02-03 | 3210.47 |  |  | 66
2003-02-02 | 3209.65 |  |  | 66
2003-02-01 | 3208.32 |  |  | 66
2003-01-31 | 3206.22 |  |  | 65
2003-01-30 | 3204.88 |  |  | 65
2003-01-29 | 3204.42 |  |  | 65
2003-01-28 | 3203.9 |  |  | 65
2003-01-27 | 3203.09 |  |  | 65
2003-01-26 | 3202.09 |  |  | 65
2003-01-25 | 3201.55 |  |  | 65
2003-01-24 | 3201.34 |  |  | 65
2003-01-23 | 3201.15 |  |  | 65
2003-01-22 | 3201.08 |  |  | 65
2003-01-21 | 3201.01 |  |  | 65
2003-01-20 | 3200.94 |  |  | 65
2003-01-19 | 3200.88 |  |  | 65
2003-01-18 | 3200.82 |  |  | 65
2003-01-17 | 3200.74 |  |  | 65
2003-01-16 | 3200.55 |  |  | 65
2003-01-15 | 3200.35 |  |  | 65
2003-01-14 | 3200.08 |  |  | 64
2003-01-13 | 3199.94 |  |  | 64
2003-01-12 | 3199.91 |  |  | 64
2003-01-11 | 3199.9 |  |  | 64
2003-01-10 | 3199.9 |  |  | 64
2003-01-09 | 3199.76 |  |  | 64
2003-01-08 | 3199.76 |  |  | 64
2003-01-07 | 3199.76 |  |  | 64
2003-01-06 | 3199.76 |  |  | 64
2003-01-05 | 3199.54 |  |  | 64
2003-01-04 | 3199.47 |  |  | 64
2003-01-03 | 3199.42 |  |  | 64
2003-01-02 | 3199.39 |  |  | 64
2003-01-01 | 3199.36 |  |  | 64
2002-12-31 | 3199.34 |  |  | 64
2002-12-30 | 3199.32 |  |  | 64
2002-12-29 | 3199.27 |  |  | 64
2002-12-28 | 3199.25 |  |  | 64
2002-12-27 | 3199.25 |  |  | 64
2002-12-26 | 3199.24 |  |  | 64
2002-12-25 | 3199.24 |  |  | 64
2002-12-24 | 3199.28 |  |  | 64
2002-12-23 | 3199.28 |  |  | 64
2002-12-22 | 3199.28 |  |  | 64
2002-12-21 | 3199.28 |  |  | 64
2002-12-20 | 3199.28 |  |  | 64
2002-12-19 | 3199.26 |  |  | 64
2002-12-18 | 3199.26 |  |  | 64
2002-12-17 | 3199.26 |  |  | 64
2002-12-16 | 3199.26 |  |  | 64
2002-12-15 | 3199.28 |  |  | 64
2002-12-14 | 3199.27 |  |  | 64
2002-12-13 | 3199.3 |  |  | 64
2002-12-12 | 3199.34 |  |  | 64
2002-12-11 | 3199.34 |  |  | 64
2002-12-10 | 3199.34 |  |  | 64
2002-12-09 | 3199.35 |  |  | 64
2002-12-08 | 3199.4 |  |  | 64
2002-12-07 | 3199.4 |  |  | 64
2002-12-06 | 3199.4 |  |  | 64
2002-12-05 | 3199.4 |  |  | 64
2002-12-04 | 3199.41 |  |  | 64
2002-12-03 | 3199.41 |  |  | 64
2002-12-02 | 3199.45 |  |  | 64
2002-12-01 | 3199.45 |  |  | 64
2002-11-30 | 3199.46 |  |  | 64
2002-11-29 | 3199.56 |  |  | 65
2002-11-28 | 3199.58 |  |  | 65
2002-11-27 | 3199.59 |  |  | 65
2002-11-26 | 3199.61 |  |  | 65
2002-11-25 | 3199.65 |  |  | 66
2002-11-24 | 3199.66 |  |  | 66
2002-11-23 | 3199.66 |  |  | 66
2002-11-22 | 3199.66 |  |  | 66
2002-11-21 | 3199.67 |  |  | 66
2002-11-20 | 3199.67 |  |  | 66
2002-11-19 | 3199.67 |  |  | 66
2002-11-18 | 3199.67 |  |  | 65
2002-11-17 | 3199.67 |  |  | 65
2002-11-16 | 3199.67 |  |  | 65
2002-11-15 | 3199.68 |  |  | 65
2002-11-14 | 3199.68 |  |  | 66
2002-11-13 | 3199.68 |  |  | 65
2002-11-12 | 3199.7 |  |  | 65
2002-11-11 | 3199.71 |  |  | 65
2002-11-10 | 3199.71 |  |  | 66
2002-11-09 | 3199.71 |  |  | 66
2002-11-08 | 3199.71 |  |  | 66
2002-11-07 | 3199.76 |  |  | 65
2002-11-06 | 3199.81 |  |  | 65
2002-11-05 | 3199.84 |  |  | 65
2002-11-04 | 3199.86 |  |  | 65
2002-11-03 | 3199.86 |  |  | 65
2002-11-02 | 3199.91 |  |  | 65
2002-11-01 | 3199.97 |  |  | 65
2002-10-31 | 3199.97 |  |  | 65
2002-10-30 | 3200.04 |  |  | 65
2002-10-29 | 3200.06 |  |  | 66
2002-10-28 | 3200.07 |  |  | 64
2002-10-27 | 3200.11 |  |  | 62
2002-10-26 | 3200.12 |  |  | 62
2002-10-25 | 3200.24 |  |  | 74
2002-10-24 | 3200.28 |  |  | 74
2002-10-23 | 3200.34 |  |  | 74
2002-10-22 | 3200.39 |  |  | 74
2002-10-21 | 3200.44 |  |  | 74
2002-10-20 | 3200.48 |  |  | 74
2002-10-19 | 3200.55 |  |  | 74
2002-10-18 | 3200.55 |  |  | 80
2002-10-17 | 3200.65 |  |  | 87
2002-10-16 | 3200.7 |  |  | 102
2002-10-15 | 3200.78 |  |  | 120
2002-10-14 | 3200.89 |  |  | 141
2002-10-13 | 3201.05 |  |  | 150
2002-10-12 | 3201.18 |  |  | 150
2002-10-11 | 3201.32 |  |  | 150
2002-10-10 | 3201.47 |  |  | 151
2002-10-09 | 3201.66 |  |  | 153
2002-10-08 | 3201.85 |  |  | 155
2002-10-07 | 3202.01 |  |  | 155
2002-10-06 | 3202.18 |  |  | 155
2002-10-05 | 3202.32 |  |  | 155
2002-10-04 | 3202.45 |  |  | 161
2002-10-03 | 3202.68 |  |  | 173
2002-10-02 | 3202.8 |  |  | 175
2002-10-01 | 3203 |  |  | 175
2002-09-30 | 3203.18 |  |  | 176
2002-09-29 | 3203.35 |  |  | 176
2002-09-28 | 3203.61 |  |  | 175
2002-09-27 | 3203.79 |  |  | 176
2002-09-26 | 3204 |  |  | 177
2002-09-25 | 3204.21 |  |  | 177
2002-09-24 | 3204.4 |  |  | 177
2002-09-23 | 3204.61 |  |  | 177
2002-09-22 | 3204.81 |  |  | 177
2002-09-21 | 3205 |  |  | 177
2002-09-20 | 3205.22 |  |  | 177
2002-09-19 | 3205.43 |  |  | 180
2002-09-18 | 3205.6 |  |  | 183
2002-09-17 | 3205.79 |  |  | 183
2002-09-16 | 3205.98 |  |  | 183
2002-09-15 | 3206.23 |  |  | 183
2002-09-14 | 3206.44 |  |  | 183
2002-09-13 | 3206.63 |  |  | 183
2002-09-12 | 3206.8 |  |  | 183
2002-09-11 | 3207 |  |  | 183
2002-09-10 | 3207.21 |  |  | 183
2002-09-09 | 3207.38 |  |  | 183
2002-09-08 | 3207.58 |  |  | 183
2002-09-07 | 3207.77 |  |  | 183
2002-09-06 | 3207.98 |  |  | 183
2002-09-05 | 3208.2 |  |  | 183
2002-09-04 | 3208.42 |  |  | 190
2002-09-03 | 3208.66 |  |  | 202
2002-09-02 | 3208.88 |  |  | 205
2002-09-01 | 3209.1 |  |  | 205
2002-08-31 | 3209.3 |  |  | 205
2002-08-30 | 3209.57 |  |  | 205
2002-08-29 | 3209.78 |  |  | 205
2002-08-28 | 3210.01 |  |  | 206
2002-08-27 | 3210.19 |  |  | 207
2002-08-26 | 3210.41 |  |  | 208
2002-08-25 | 3210.59 |  |  | 209
2002-08-24 | 3210.79 |  |  | 209
2002-08-23 | 3211 |  |  | 209
2002-08-22 | 3211.26 |  |  | 209
2002-08-21 | 3211.45 |  |  | 210
2002-08-20 | 3211.66 |  |  | 211
2002-08-19 | 3211.92 |  |  | 211
2002-08-18 | 3212.16 |  |  | 211
2002-08-17 | 3212.38 |  |  | 211
2002-08-16 | 3212.61 |  |  | 211
2002-08-15 | 3212.83 |  |  | 211
2002-08-14 | 3213.09 |  |  | 211
2002-08-13 | 3213.28 |  |  | 211
2002-08-12 | 3213.46 |  |  | 211
2002-08-11 | 3213.7 |  |  | 211
2002-08-10 | 3213.94 |  |  | 212
2002-08-09 | 3214.14 |  |  | 213
2002-08-08 | 3214.32 |  |  | 213
2002-08-07 | 3214.55 |  |  | 213
2002-08-06 | 3214.7 |  |  | 213
2002-08-05 | 3214.92 |  |  | 213
2002-08-04 | 3215.13 |  |  | 213
2002-08-03 | 3215.35 |  |  | 213
2002-08-02 | 3215.58 |  |  | 213
2002-08-01 | 3215.82 |  |  | 213
2002-07-31 | 3216.04 |  |  | 213
2002-07-30 | 3216.29 |  |  | 213
2002-07-29 | 3216.53 |  |  | 214
2002-07-28 | 3216.7 |  |  | 215
2002-07-27 | 3216.92 |  |  | 215
2002-07-26 | 3217.18 |  |  | 215
2002-07-25 | 3217.42 |  |  | 215
2002-07-24 | 3217.66 |  |  | 215
2002-07-23 | 3217.83 |  |  | 215
2002-07-22 | 3218.01 |  |  | 215
2002-07-21 | 3218.17 |  |  | 215
2002-07-20 | 3218.38 |  |  | 215
2002-07-19 | 3218.58 |  |  | 215
2002-07-18 | 3218.79 |  |  | 215
2002-07-17 | 3219.08 |  |  | 216
2002-07-16 | 3219.27 |  |  | 217
2002-07-15 | 3219.46 |  |  | 217
2002-07-14 | 3219.68 |  |  | 217
2002-07-13 | 3219.93 |  |  | 217
2002-07-12 | 3220.09 |  |  | 217
2002-07-11 | 3220.36 |  |  | 217
2002-07-10 | 3220.53 |  |  | 217
2002-07-09 | 3220.71 |  |  | 217
2002-07-08 | 3220.88 |  |  | 217
2002-07-07 | 3221.08 |  |  | 218
2002-07-06 | 3221.22 |  |  | 218
2002-07-05 | 3221.35 |  |  | 218
2002-07-04 | 3221.56 |  |  | 218
2002-07-03 | 3221.76 |  |  | 218
2002-07-02 | 3222 |  |  | 218
2002-07-01 | 3222.16 |  |  | 218
2002-06-30 | 3222.35 |  |  | 219
2002-06-29 | 3222.56 |  |  | 219
2002-06-28 | 3222.73 |  |  | 219
2002-06-27 | 3222.98 |  |  | 219
2002-06-26 | 3223.22 |  |  | 219
2002-06-25 | 3223.39 |  |  | 219
2002-06-24 | 3223.54 |  |  | 220
2002-06-23 | 3223.73 |  |  | 220
2002-06-22 | 3223.87 |  |  | 220
2002-06-21 | 3224.03 |  |  | 220
2002-06-20 | 3224.23 |  |  | 220
2002-06-19 | 3224.38 |  |  | 220
2002-06-18 | 3224.49 |  |  | 220
2002-06-17 | 3224.7 |  |  | 220
2002-06-16 | 3224.87 |  |  | 220
2002-06-15 | 3225.09 |  |  | 220
2002-06-14 | 3225.24 |  |  | 220
2002-06-13 | 3225.41 |  |  | 220
2002-06-12 | 3225.56 |  |  | 220
2002-06-11 | 3225.7 |  |  | 220
2002-06-10 | 3225.82 |  |  | 220
2002-06-09 | 3225.99 |  |  | 220
2002-06-08 | 3226.18 |  |  | 220
2002-06-07 | 3226.38 |  |  | 221
2002-06-06 | 3226.63 |  |  | 221
2002-06-05 | 3226.82 |  |  | 221
2002-06-04 | 3226.98 |  |  | 222
2002-06-03 | 3227.15 |  |  | 222
2002-06-02 | 3227.28 |  |  | 222
2002-06-01 | 3227.45 |  |  | 222
2002-05-31 | 3227.57 |  |  | 222
2002-05-30 | 3227.72 |  |  | 222
2002-05-29 | 3227.88 |  |  | 222
2002-05-28 | 3228.03 |  |  | 222
2002-05-27 | 3228.14 |  |  | 222
2002-05-26 | 3228.26 |  |  | 222
2002-05-25 | 3228.36 |  |  | 223
2002-05-24 | 3228.52 |  |  | 222
2002-05-23 | 3228.66 |  |  | 222
2002-05-22 | 3228.77 |  |  | 223
2002-05-21 | 3228.92 |  |  | 224
2002-05-20 | 3229.04 |  |  | 224
2002-05-19 | 3229.18 |  |  | 224
2002-05-18 | 3229.35 |  |  | 224
2002-05-17 | 3229.51 |  |  | 224
2002-05-16 | 3229.68 |  |  | 224
2002-05-15 | 3229.74 |  |  | 224
2002-05-14 | 3229.91 |  |  | 224
2002-05-13 | 3230.02 |  |  | 224
2002-05-12 | 3230.16 |  |  | 224
2002-05-11 | 3230.25 |  |  | 224
2002-05-10 | 3230.35 |  |  | 224
2002-05-09 | 3230.43 |  |  | 224
2002-05-08 | 3230.52 |  |  | 225
2002-05-07 | 3230.7 |  |  | 226
2002-05-06 | 3230.79 |  |  | 226
2002-05-05 | 3230.92 |  |  | 226
2002-05-04 | 3230.99 |  |  | 226
2002-05-03 | 3231.11 |  |  | 226
2002-05-02 | 3231.22 |  |  | 225
2002-05-01 | 3231.28 |  |  | 224
2002-04-30 | 3231.32 |  |  | 224
2002-04-29 | 3231.38 |  |  | 224
2002-04-28 | 3231.38 |  |  | 224
2002-04-27 | 3231.38 |  |  | 224
2002-04-26 | 3231.38 |  |  | 224
2002-04-25 | 3231.34 |  |  | 207
2002-04-24 | 3231.28 |  |  | 183
2002-04-23 | 3231.23 |  |  | 171
2002-04-22 | 3231.15 |  |  | 148
2002-04-21 | 3230.97 |  |  | 148
2002-04-20 | 3230.82 |  |  | 148
2002-04-19 | 3230.58 |  |  | 148
2002-04-18 | 3230.3 |  |  | 148
2002-04-17 | 3229.82 |  |  | 148
2002-04-16 | 3229.46 |  |  | 148
2002-04-15 | 3228.88 |  |  | 148
2002-04-14 | 3228.06 |  |  | 148
2002-04-13 | 3227.42 |  |  | 147
2002-04-12 | 3226.88 |  |  | 147
2002-04-11 | 3226.33 |  |  | 147
2002-04-10 | 3225.76 |  |  | 146
2002-04-09 | 3225.13 |  |  | 145
2002-04-08 | 3224.62 |  |  | 145
2002-04-07 | 3223.94 |  |  | 145
2002-04-06 | 3223.24 |  |  | 144
2002-04-05 | 3222.37 |  |  | 143
2002-04-04 | 3221.46 |  |  | 142
2002-04-03 | 3220.53 |  |  | 142
2002-04-02 | 3219.49 |  |  | 142
2002-04-01 | 3218.3 |  |  | 141
2002-03-31 | 3217.22 |  |  | 81
2002-03-30 | 3216.06 |  |  | 66
2002-03-29 | 3214.98 |  |  | 66
2002-03-28 | 3213.97 |  |  | 65
2002-03-27 | 3213.05 |  |  | 65
2002-03-26 | 3212.16 |  |  | 65
2002-03-25 | 3211.42 |  |  | 65
2002-03-24 | 3210.81 |  |  | 65
2002-03-23 | 3210.17 |  |  | 64
2002-03-22 | 3209.77 |  |  | 64
2002-03-21 | 3209.45 |  |  | 64
2002-03-20 | 3209.22 |  |  | 64
2002-03-19 | 3209.03 |  |  | 64
2002-03-18 | 3208.86 |  |  | 64
2002-03-17 | 3208.67 |  |  | 64
2002-03-16 | 3208.46 |  |  | 64
2002-03-15 | 3208.27 |  |  | 63
2002-03-14 | 3208.05 |  |  | 63
2002-03-13 | 3207.63 |  |  | 63
2002-03-12 | 3207.26 |  |  | 63
2002-03-11 | 3206.97 |  |  | 63
2002-03-10 | 3206.81 |  |  | 63
2002-03-09 | 3206.62 |  |  | 63
2002-03-08 | 3206.46 |  |  | 63
2002-03-07 | 3206.28 |  |  | 63
2002-03-06 | 3206.02 |  |  | 63
2002-03-05 | 3205.86 |  |  | 63
2002-03-04 | 3205.67 |  |  | 63
2002-03-03 | 3205.55 |  |  | 63
2002-03-02 | 3205.41 |  |  | 63
2002-03-01 | 3205.23 |  |  | 63
2002-02-28 | 3205 |  |  | 63
2002-02-27 | 3204.68 |  |  | 63
2002-02-26 | 3204.35 |  |  | 63
2002-02-25 | 3203.96 |  |  | 63
2002-02-24 | 3203.46 |  |  | 62
2002-02-23 | 3202.87 |  |  | 62
2002-02-22 | 3202.51 |  |  | 62
2002-02-21 | 3202.27 |  |  | 62
2002-02-20 | 3202.11 |  |  | 62
2002-02-19 | 3202 |  |  | 62
2002-02-18 | 3201.93 |  |  | 62
2002-02-17 | 3201.85 |  |  | 62
2002-02-16 | 3201.8 |  |  | 62
2002-02-15 | 3201.74 |  |  | 62
2002-02-14 | 3201.66 |  |  | 62
2002-02-13 | 3201.62 |  |  | 62
2002-02-12 | 3201.59 |  |  | 62
2002-02-11 | 3201.51 |  |  | 62
2002-02-10 | 3201.48 |  |  | 62
2002-02-09 | 3201.41 |  |  | 61
2002-02-08 | 3201.35 |  |  | 62
2002-02-07 | 3201.28 |  |  | 61
2002-02-06 | 3201.24 |  |  | 61
2002-02-05 | 3201.17 |  |  | 61
2002-02-04 | 3201.14 |  |  | 61
2002-02-03 | 3201.11 |  |  | 61
2002-02-02 | 3201.07 |  |  | 61
2002-02-01 | 3201.01 |  |  | 61
2002-01-31 | 3200.94 |  |  | 61
2002-01-30 | 3200.86 |  |  | 60
2002-01-29 | 3200.82 |  |  | 60
2002-01-28 | 3200.81 |  |  | 61
2002-01-27 | 3200.8 |  |  | 61
2002-01-26 | 3200.72 |  |  | 61
2002-01-25 | 3200.6 |  |  | 61
2002-01-24 | 3200.5 |  |  | 60
2002-01-23 | 3200.39 |  |  | 60
2002-01-22 | 3200.33 |  |  | 60
2002-01-21 | 3200.15 |  |  | 59
2002-01-20 | 3200.05 |  |  | 59
2002-01-19 | 3199.91 |  |  | 59
2002-01-18 | 3199.81 |  |  | 59
2002-01-17 | 3199.65 |  |  | 59
2002-01-16 | 3199.54 |  |  | 59
2002-01-15 | 3199.38 |  |  | 59
2002-01-14 | 3199.15 |  |  | 59
2002-01-13 | 3198.88 |  |  | 59
2002-01-12 | 3198.52 |  |  | 59
2002-01-11 | 3198.06 |  |  | 59
2002-01-10 | 3197.4 |  |  | 62
2002-01-09 | 3196.57 |  |  | 62
2002-01-08 | 3195.26 |  |  | 62
2002-01-07 | 3193.52 |  |  | 62
2002-01-06 | 3192.39 |  |  | 62
2002-01-05 | 3192 |  |  | 61
2002-01-04 | 3191.54 |  |  | 61
2002-01-03 | 3190.78 |  |  | 60
2002-01-02 | 3190.04 |  |  | 60
2002-01-01 | 3189.85 |  |  | 60
2001-12-31 | 3189.66 |  |  | 60
2001-12-30 | 3189.54 |  |  | 60
2001-12-29 | 3189.46 |  |  | 60
2001-12-28 | 3189.42 |  |  | 60
2001-12-27 | 3189.32 |  |  | 60
2001-12-26 | 3189.26 |  |  | 60
2001-12-25 | 3189.24 |  |  | 60
2001-12-24 | 3189.2 |  |  | 60
2001-12-23 | 3189.12 |  |  | 60
2001-12-22 | 3189.11 |  |  | 60
2001-12-21 | 3189.06 |  |  | 60
2001-12-20 | 3188.91 |  |  | 60
2001-12-19 | 3188.78 |  |  | 60
2001-12-18 | 3188.58 |  |  | 60
2001-12-17 | 3188.46 |  |  | 59
2001-12-16 | 3188.2 |  |  | 59
2001-12-15 | 3188.06 |  |  | 59
2001-12-14 | 3187.9 |  |  | 59
2001-12-13 | 3187.8 |  |  | 59
2001-12-12 | 3187.76 |  |  | 59
2001-12-11 | 3187.64 |  |  | 59
2001-12-10 | 3187.59 |  |  | 59
2001-12-09 | 3187.58 |  |  | 59
2001-12-08 | 3187.53 |  |  | 59
2001-12-07 | 3187.47 |  |  | 55
2001-12-06 | 3187.38 |  |  | 52
2001-12-05 | 3187.31 |  |  | 52
2001-12-04 | 3187.26 |  |  | 52
2001-12-03 | 3187.22 |  |  | 52
2001-12-02 | 3187.19 |  |  | 52
2001-12-01 | 3187.14 |  |  | 52
2001-11-30 | 3187.12 |  |  | 52
2001-11-29 | 3187.08 |  |  | 52
2001-11-28 | 3187.08 |  |  | 52
2001-11-27 | 3187.01 |  |  | 52
2001-11-26 | 3186.99 |  |  | 52
2001-11-25 | 3186.99 |  |  | 52
2001-11-24 | 3186.98 |  |  | 52
2001-11-23 | 3186.97 |  |  | 52
2001-11-22 | 3186.87 |  |  | 52
2001-11-21 | 3186.86 |  |  | 52
2001-11-20 | 3186.86 |  |  | 52
2001-11-19 | 3186.86 |  |  | 52
2001-11-18 | 3186.84 |  |  | 52
2001-11-17 | 3186.84 |  |  | 52
2001-11-16 | 3186.84 |  |  | 52
2001-11-15 | 3186.82 |  |  | 52
2001-11-14 | 3186.82 |  |  | 52
2001-11-13 | 3186.82 |  |  | 52
2001-11-12 | 3186.82 |  |  | 51
2001-11-11 | 3186.83 |  |  | 51
2001-11-10 | 3186.85 |  |  | 51
2001-11-09 | 3186.87 |  |  | 51
2001-11-08 | 3186.88 |  |  | 50
2001-11-07 | 3186.88 |  |  | 50
2001-11-06 | 3186.88 |  |  | 50
2001-11-05 | 3186.89 |  |  | 50
2001-11-04 | 3186.89 |  |  | 49
2001-11-03 | 3186.89 |  |  | 49
2001-11-02 | 3186.89 |  |  | 49
2001-11-01 | 3186.81 |  |  | 49
2001-10-31 | 3186.81 |  |  | 49
2001-10-30 | 3186.81 |  |  | 49
2001-10-29 | 3186.81 |  |  | 49
2001-10-28 | 3186.81 |  |  | 49
2001-10-27 | 3186.84 |  |  | 48
2001-10-26 | 3186.86 |  |  | 48
2001-10-25 | 3186.86 |  |  | 48
2001-10-24 | 3186.86 |  |  | 56
2001-10-23 | 3186.91 |  |  | 68
2001-10-22 | 3186.97 |  |  | 68
2001-10-21 | 3187.03 |  |  | 68
2001-10-20 | 3187.08 |  |  | 68
2001-10-19 | 3187.11 |  |  | 78
2001-10-18 | 3187.21 |  |  | 96
2001-10-17 | 3187.29 |  |  | 96
2001-10-16 | 3187.4 |  |  | 96
2001-10-15 | 3187.46 |  |  | 111
2001-10-14 | 3187.62 |  |  | 125
2001-10-13 | 3187.77 |  |  | 125
2001-10-12 | 3187.89 |  |  | 125
2001-10-11 | 3188.04 |  |  | 125
2001-10-10 | 3188.21 |  |  | 124
2001-10-09 | 3188.4 |  |  | 124
2001-10-08 | 3188.54 |  |  | 123
2001-10-07 | 3188.75 |  |  | 123
2001-10-06 | 3188.94 |  |  | 122
2001-10-05 | 3189.13 |  |  | 121
2001-10-04 | 3189.32 |  |  | 122
2001-10-03 | 3189.46 |  |  | 122
2001-10-02 | 3189.67 |  |  | 122
2001-10-01 | 3189.86 |  |  | 124
2001-09-30 | 3190.04 |  |  | 138.22
2001-09-29 | 3190.22 |  |  | 138.22
2001-09-28 | 3190.37 |  |  | 143.17
2001-09-27 | 3190.61 |  |  | 151.82
2001-09-26 | 3190.79 |  |  | 151.82
2001-09-25 | 3190.98 |  |  | 151.83
2001-09-24 | 3191.16 |  |  | 160.93
2001-09-23 | 3191.37 |  |  | 173.57
2001-09-22 | 3191.61 |  |  | 173.57
2001-09-21 | 3191.85 |  |  | 173.57
2001-09-20 | 3192.08 |  |  | 173.57
2001-09-19 | 3192.32 |  |  | 174.37
2001-09-18 | 3192.55 |  |  | 175.46
2001-09-17 | 3192.78 |  |  | 175.46
2001-09-16 | 3193 |  |  | 175.46
2001-09-15 | 3193.27 |  |  | 175.46
2001-09-14 | 3193.46 |  |  | 175.46
2001-09-13 | 3193.7 |  |  | 175.46
2001-09-12 | 3193.93 |  |  | 183.58
2001-09-11 | 3194.15 |  |  | 196.47
2001-09-10 | 3194.39 |  |  | 203.47
2001-09-09 | 3194.67 |  |  | 203.47
2001-09-08 | 3194.93 |  |  | 203.47
2001-09-07 | 3195.19 |  |  | 207.67
2001-09-06 | 3195.45 |  |  | 214.68
2001-09-05 | 3195.74 |  |  | 214.68
2001-09-04 | 3196.05 |  |  | 214.68
2001-09-03 | 3196.34 |  |  | 214.68
2001-09-02 | 3196.65 |  |  | 214.68
2001-09-01 | 3196.92 |  |  | 214.68
2001-08-31 | 3197.21 |  |  | 214.68
2001-08-30 | 3197.51 |  |  | 214.68
2001-08-29 | 3197.78 |  |  | 214.75
2001-08-28 | 3198.02 |  |  | 216.58
2001-08-27 | 3198.32 |  |  | 216.58
2001-08-26 | 3198.6 |  |  | 216.58
2001-08-25 | 3198.84 |  |  | 216.58
2001-08-24 | 3199.1 |  |  | 223.61
2001-08-23 | 3199.39 |  |  | 234.39
2001-08-22 | 3199.72 |  |  | 234.39
2001-08-21 | 3200 |  |  | 234.39
2001-08-20 | 3200.28 |  |  | 234.39
2001-08-19 | 3200.6 |  |  | 234.39
2001-08-18 | 3200.9 |  |  | 234.39
2001-08-17 | 3201.19 |  |  | 227.69
2001-08-16 | 3201.36 |  |  | 222.35
2001-08-15 | 3201.65 |  |  | 222.49
2001-08-14 | 3201.93 |  |  | 223.4
2001-08-13 | 3202.18 |  |  | 224.2
2001-08-12 | 3202.45 |  |  | 224.26
2001-08-11 | 3202.74 |  |  | 224.26
2001-08-10 | 3203.02 |  |  | 224.26
2001-08-09 | 3203.26 |  |  | 224.26
2001-08-08 | 3203.56 |  |  | 224.26
2001-08-07 | 3203.8 |  |  | 224.48
2001-08-06 | 3204.06 |  |  | 225.39
2001-08-05 | 3204.29 |  |  | 226.09
2001-08-04 | 3204.55 |  |  | 226.2
2001-08-03 | 3204.79 |  |  | 226.2
2001-08-02 | 3205.06 |  |  | 226.2
2001-08-01 | 3205.32 |  |  | 226.22
2001-07-31 | 3205.57 |  |  | 226.2
2001-07-30 | 3205.81 |  |  | 227.69
2001-07-29 | 3206.07 |  |  | 228.23
2001-07-28 | 3206.32 |  |  | 228.23
2001-07-27 | 3206.59 |  |  | 228.27
2001-07-26 | 3206.84 |  |  | 228.23
2001-07-25 | 3207.1 |  |  | 228.23
2001-07-24 | 3207.34 |  |  | 243.48
2001-07-23 | 3207.62 |  |  | 255.52
2001-07-22 | 3207.86 |  |  | 255.54
2001-07-21 | 3208.14 |  |  | 255.54
2001-07-20 | 3208.44 |  |  | 255.77
2001-07-19 | 3208.63 |  |  | 255.58
2001-07-18 | 3208.87 |  |  | 256.63
2001-07-17 | 3209.16 |  |  | 257.67
2001-07-16 | 3209.46 |  |  | 257.71
2001-07-15 | 3209.75 |  |  | 257.71
2001-07-14 | 3210.05 |  |  | 257.71
2001-07-13 | 3210.33 |  |  | 257.71
2001-07-12 | 3210.59 |  |  | 254.25
2001-07-11 | 3210.87 |  |  | 249.11
2001-07-10 | 3211.12 |  |  | 232.99
2001-07-09 | 3211.41 |  |  | 214.68
2001-07-08 | 3211.6 |  |  | 214.68
2001-07-07 | 3211.82 |  |  | 214.68
2001-07-06 | 3212.06 |  |  | 214.68
2001-07-05 | 3212.28 |  |  | 214.68
2001-07-04 | 3212.53 |  |  | 214.68
2001-07-03 | 3212.72 |  |  | 214.68
2001-07-02 | 3212.91 |  |  | 214.68
2001-07-01 | 3213.13 |  |  | 214.68
2001-06-30 | 3213.33 |  |  | 214.68
2001-06-29 | 3213.51 |  |  | 214.68
2001-06-28 | 3213.73 |  |  | 214.68
2001-06-27 | 3213.95 |  |  | 216.05
2001-06-26 | 3214.15 |  |  | 216.58
2001-06-25 | 3214.32 |  |  | 216.58
2001-06-24 | 3214.53 |  |  | 216.58
2001-06-23 | 3214.72 |  |  | 216.58
2001-06-22 | 3214.95 |  |  | 217.44
2001-06-21 | 3215.15 |  |  | 218.48
2001-06-20 | 3215.34 |  |  | 218.48
2001-06-19 | 3215.53 |  |  | 218.48
2001-06-18 | 3215.72 |  |  | 218.48
2001-06-17 | 3215.91 |  |  | 218.48
2001-06-16 | 3216.11 |  |  | 218.48
2001-06-15 | 3216.33 |  |  | 218.48
2001-06-14 | 3216.56 |  |  | 218.48
2001-06-13 | 3216.72 |  |  | 218.48
2001-06-12 | 3216.91 |  |  | 218.48
2001-06-11 | 3217.13 |  |  | 219.53
2001-06-10 | 3217.33 |  |  | 220.4
2001-06-09 | 3217.54 |  |  | 220.4
2001-06-08 | 3217.73 |  |  | 220.4
2001-06-07 | 3217.9 |  |  | 220.4
2001-06-06 | 3218.09 |  |  | 220.4
2001-06-05 | 3218.26 |  |  | 220.4
2001-06-04 | 3218.44 |  |  | 220.4
2001-06-03 | 3218.63 |  |  | 221.87
2001-06-02 | 3218.82 |  |  | 222.32
2001-06-01 | 3219.05 |  |  | 222.32
2001-05-31 | 3219.28 |  |  | 222.32
2001-05-30 | 3219.46 |  |  | 222.32
2001-05-29 | 3219.63 |  |  | 222.32
2001-05-28 | 3219.84 |  |  | 222.32
2001-05-27 | 3220.05 |  |  | 222.32
2001-05-26 | 3220.31 |  |  | 222.32
2001-05-25 | 3220.47 |  |  | 222.32
2001-05-24 | 3220.63 |  |  | 222.32
2001-05-23 | 3220.85 |  |  | 222.32
2001-05-22 | 3220.96 |  |  | 222.32
2001-05-21 | 3221.08 |  |  | 222.32
2001-05-20 | 3221.18 |  |  | 222.32
2001-05-19 | 3221.31 |  |  | 222.32
2001-05-18 | 3221.43 |  |  | 222.32
2001-05-17 | 3221.57 |  |  | 219.9
2001-05-16 | 3221.66 |  |  | 209.03
2001-05-15 | 3221.71 |  |  | 209.03
2001-05-14 | 3222 |  |  | 209.03
2001-05-13 | 3222.16 |  |  | 209.03
2001-05-12 | 3222.3 |  |  | 209.03
2001-05-11 | 3222.4 |  |  | 209.03
2001-05-10 | 3222.54 |  |  | 209.03
2001-05-09 | 3222.65 |  |  | 199.72
2001-05-08 | 3222.73 |  |  | 184.86
2001-05-07 | 3222.75 |  |  | 183.13
2001-05-06 | 3222.75 |  |  | 183.13
2001-05-05 | 3222.75 |  |  | 183.13
2001-05-04 | 3222.75 |  |  | 183.13
2001-05-03 | 3222.71 |  |  | 164.09
2001-05-02 | 3222.59 |  |  | 138.22
2001-05-01 | 3222.46 |  |  | 138.22
2001-04-30 | 3222.26 |  |  | 138.11
2001-04-29 | 3222.09 |  |  | 137.36
2001-04-28 | 3221.84 |  |  | 136.59
2001-04-27 | 3221.61 |  |  | 136.57
2001-04-26 | 3221.35 |  |  | 136.57
2001-04-25 | 3221.12 |  |  | 136.57
2001-04-24 | 3220.94 |  |  | 118.39
2001-04-23 | 3220.76 |  |  | 100.87
2001-04-22 | 3220.62 |  |  | 100.75
2001-04-21 | 3220.44 |  |  | 100.43
2001-04-20 | 3220.28 |  |  | 107.43
2001-04-19 | 3220.11 |  |  | 116.81
2001-04-18 | 3219.98 |  |  | 116.14
2001-04-17 | 3219.96 |  |  | 101.24
2001-04-16 | 3219.92 |  |  | 92.43
2001-04-15 | 3219.86 |  |  | 92.28
2001-04-14 | 3219.8 |  |  | 92.21
2001-04-13 | 3219.73 |  |  | 86.03
2001-04-12 | 3219.66 |  |  | 75.99
2001-04-11 | 3219.56 |  |  | 86
2001-04-10 | 3219.48 |  |  | 100.36
2001-04-09 | 3219.43 |  |  | 100.32
2001-04-08 | 3219.37 |  |  | 100.32
2001-04-07 | 3219.33 |  |  | 100.34
2001-04-06 | 3219.21 |  |  | 110.52
2001-04-05 | 3219.08 |  |  | 116.14
2001-04-04 | 3218.94 |  |  | 116.14
2001-04-03 | 3218.74 |  |  | 116.14
2001-04-02 | 3218.48 |  |  | 116.14
2001-04-01 | 3218.13 |  |  | 116.14
2001-03-31 | 3217.73 |  |  | 115.4
2001-03-30 | 3217.37 |  |  | 115.07
2001-03-29 | 3216.85 |  |  | 101.67
2001-03-28 | 3216.15 |  |  | 61.51
2001-03-27 | 3215.62 |  |  | 61.51
2001-03-26 | 3215.01 |  |  | 61.51
2001-03-25 | 3214 |  |  | 61.49
2001-03-24 | 3212.94 |  |  | 60.59
2001-03-23 | 3212.21 |  |  | 60.47
2001-03-22 | 3211.62 |  |  | 60.47
2001-03-21 | 3211.22 |  |  | 60.47
2001-03-20 | 3210.81 |  |  | 60.47
2001-03-19 | 3210.35 |  |  | 60.47
2001-03-18 | 3210.13 |  |  | 60.47
2001-03-17 | 3210.04 |  |  | 60.47
2001-03-16 | 3209.95 |  |  | 60.47
2001-03-15 | 3209.84 |  |  | 60.47
2001-03-14 | 3209.68 |  |  | 60.47
2001-03-13 | 3209.55 |  |  | 60.47
2001-03-12 | 3209.41 |  |  | 60.47
2001-03-11 | 3209.24 |  |  | 60.4
2001-03-10 | 3209.14 |  |  | 60.33
2001-03-09 | 3208.96 |  |  | 60.43
2001-03-08 | 3208.82 |  |  | 60.46
2001-03-07 | 3208.62 |  |  | 60.02
2001-03-06 | 3208.55 |  |  | 59.94
2001-03-05 | 3208.52 |  |  | 59.47
2001-03-04 | 3208.52 |  |  | 59.63
2001-03-03 | 3208.45 |  |  | 59.52
2001-03-02 | 3208.43 |  |  | 59.48
2001-03-01 | 3208.41 |  |  | 59.05
2001-02-28 | 3208.4 |  |  | 58.41
2001-02-27 | 3208.33 |  |  | 58.41
2001-02-26 | 3208.29 |  |  | 58.41
2001-02-25 | 3208.27 |  |  | 58.41
2001-02-24 | 3208.2 |  |  | 58.41
2001-02-23 | 3208.09 |  |  | 58.41
2001-02-22 | 3208.04 |  |  | 58.5
2001-02-21 | 3207.97 |  |  | 58.46
2001-02-20 | 3207.95 |  |  | 58.41
2001-02-19 | 3207.88 |  |  | 58.41
2001-02-18 | 3207.88 |  |  | 58.41
2001-02-17 | 3207.87 |  |  | 58.41
2001-02-16 | 3207.87 |  |  | 59.22
2001-02-15 | 3207.82 |  |  | 59.44
2001-02-14 | 3207.81 |  |  | 59.44
2001-02-13 | 3207.79 |  |  | 59.44
2001-02-12 | 3207.77 |  |  | 59.44
2001-02-11 | 3207.75 |  |  | 59.44
2001-02-10 | 3207.74 |  |  | 59.44
2001-02-09 | 3207.68 |  |  | 59.44
2001-02-08 | 3207.67 |  |  | 59.44
2001-02-07 | 3207.65 |  |  | 59.44
2001-02-06 | 3207.6 |  |  | 59.44
2001-02-05 | 3207.56 |  |  | 59.44
2001-02-04 | 3207.54 |  |  | 59.44
2001-02-03 | 3207.53 |  |  | 59.44
2001-02-02 | 3207.51 |  |  | 59.44
2001-02-01 | 3207.49 |  |  | 59.44
2001-01-31 | 3207.49 |  |  | 59.44
2001-01-30 | 3207.48 |  |  | 59.44
2001-01-29 | 3207.48 |  |  | 59.44
2001-01-28 | 3207.47 |  |  | 59.44
2001-01-27 | 3207.43 |  |  | 59.44
2001-01-26 | 3207.43 |  |  | 59.44
2001-01-25 | 3207.43 |  |  | 59.44
2001-01-24 | 3207.42 |  |  | 59.44
2001-01-23 | 3207.42 |  |  | 59.44
2001-01-22 | 3207.42 |  |  | 58.88
2001-01-21 | 3207.42 |  |  | 55.49
2001-01-20 | 3207.42 |  |  | 55.49
2001-01-19 | 3207.42 |  |  | 54.93
2001-01-18 | 3207.3 |  |  | 54.59
2001-01-17 | 3207.3 |  |  | 54.59
2001-01-16 | 3207.3 |  |  | 54.59
2001-01-15 | 3207.3 |  |  | 54.59
2001-01-14 | 3207.3 |  |  | 54.59
2001-01-13 | 3207.3 |  |  | 54.6
2001-01-12 | 3207.3 |  |  | 54.59
2001-01-11 | 3207.29 |  |  | 54.59
2001-01-10 | 3207.29 |  |  | 54.61
2001-01-09 | 3207.26 |  |  | 54.63
2001-01-08 | 3207.25 |  |  | 54.59
2001-01-07 | 3207.25 |  |  | 54.59
2001-01-06 | 3207.25 |  |  | 57.7
2001-01-05 | 3207.25 |  |  | 64.7
2001-01-04 | 3207.24 |  |  | 64.7
2001-01-03 | 3207.24 |  |  | 64.7
2001-01-02 | 3207.24 |  |  | 64.73
2001-01-01 | 3207.24 |  |  | 64.7
2000-12-31 | 3207.23 |  |  | 64.7
2000-12-30 | 3207.22 |  |  | 64.7
2000-12-29 | 3207.22 |  |  | 64.73
2000-12-28 | 3207.21 |  |  | 64.7
2000-12-27 | 3207.21 |  |  | 64.73
2000-12-26 | 3207.21 |  |  | 64.88
2000-12-25 | 3207.21 |  |  | 64.86
2000-12-24 | 3207.17 |  |  | 65.29
2000-12-23 | 3207.17 |  |  | 65.52
2000-12-22 | 3207.16 |  |  | 65
2000-12-21 | 3207.15 |  |  | 65.31
2000-12-20 | 3207.14 |  |  | 64.78
2000-12-19 | 3207.14 |  |  | 64.72
2000-12-18 | 3207.14 |  |  | 64.8
2000-12-17 | 3207.14 |  |  | 65.2
2000-12-16 | 3207.14 |  |  | 65.02
2000-12-15 | 3207.14 |  |  | 64.98
2000-12-14 | 3207.13 |  |  | 64.83
2000-12-13 | 3207.13 |  |  | 64.86
2000-12-12 | 3207.13 |  |  | 64.7
2000-12-11 | 3207.13 |  |  | 64.89
2000-12-10 | 3207.13 |  |  | 64.74
2000-12-09 | 3207.13 |  |  | 64.7
2000-12-08 | 3207.13 |  |  | 64.7
2000-12-07 | 3207.16 |  |  | 64.7
2000-12-06 | 3207.16 |  |  | 64.7
2000-12-05 | 3207.16 |  |  | 64.7
2000-12-04 | 3207.16 |  |  | 64.7
2000-12-03 | 3207.08 |  |  | 64.76
2000-12-02 | 3207.08 |  |  | 64.7
2000-12-01 | 3207.08 |  |  | 64.73
2000-11-30 | 3207.08 |  |  | 64.7
2000-11-29 | 3207.08 |  |  | 64.75
2000-11-28 | 3207.08 |  |  | 64.7
2000-11-27 | 3207.08 |  |  | 64.7
2000-11-26 | 3207.08 |  |  | 64.7
2000-11-25 | 3207.08 |  |  | 64.7
2000-11-24 | 3207.08 |  |  | 64.7
2000-11-23 | 3207.08 |  |  | 64.7
2000-11-22 | 3207.08 |  |  | 64.7
2000-11-21 | 3207.08 |  |  | 64.7
2000-11-20 | 3207.08 |  |  | 64.7
2000-11-19 | 3207.08 |  |  | 64.7
2000-11-18 | 3207.09 |  |  | 64.7
2000-11-17 | 3207.09 |  |  | 64.73
2000-11-16 | 3207.09 |  |  | 64.7
2000-11-15 | 3207.09 |  |  | 64.7
2000-11-14 | 3207.09 |  |  | 64.7
2000-11-13 | 3207.09 |  |  | 64.72
2000-11-12 | 3207.11 |  |  | 64.7
2000-11-11 | 3207.11 |  |  | 64.87
2000-11-10 | 3207.11 |  |  | 65.49
2000-11-09 | 3207.11 |  |  | 65.62
2000-11-08 | 3207.11 |  |  | 65.74
2000-11-07 | 3207.11 |  |  | 65
2000-11-06 | 3207.11 |  |  | 65.41
2000-11-05 | 3207.11 |  |  | 65.45
2000-11-04 | 3207.11 |  |  | 65.31
2000-11-03 | 3207.11 |  |  | 64.71
2000-11-02 | 3207.11 |  |  | 64.7
2000-11-01 | 3207.11 |  |  | 64.7
2000-10-31 | 3207.11 |  |  | 64.7
2000-10-30 | 3207.09 |  |  | 65.58
2000-10-29 | 3206.82 |  |  | 65.78
2000-10-28 | 3206.82 |  |  | 65.83
2000-10-27 | 3206.82 |  |  | 65.78
2000-10-26 | 3206.89 |  |  | 65.78
2000-10-25 | 3206.89 |  |  | 65.78
2000-10-24 | 3206.91 |  |  | 65.78
2000-10-23 | 3206.92 |  |  | 65.78
2000-10-22 | 3206.95 |  |  | 65.78
2000-10-21 | 3206.96 |  |  | 65.78
2000-10-20 | 3206.97 |  |  | 65.78
2000-10-19 | 3207.02 |  |  | 65.78
2000-10-18 | 3207.03 |  |  | 65.78
2000-10-17 | 3207.04 |  |  | 77.64
2000-10-16 | 3207.12 |  |  | 95.1
2000-10-15 | 3207.18 |  |  | 89.6
2000-10-14 | 3207.25 |  |  | 89.6
2000-10-13 | 3207.31 |  |  | 109.17
2000-10-12 | 3207.36 |  |  | 123.78
2000-10-11 | 3207.46 |  |  | 123.78
2000-10-10 | 3207.53 |  |  | 138.87
2000-10-09 | 3207.63 |  |  | 157.1
2000-10-08 | 3207.81 |  |  | 157.1
2000-10-07 | 3207.95 |  |  | 157.1
2000-10-06 | 3208.08 |  |  | 157.1
2000-10-05 | 3208.22 |  |  | 157.1
2000-10-04 | 3208.39 |  |  | 157.1
2000-10-03 | 3208.53 |  |  | 157.1
2000-10-02 | 3208.68 |  |  | 157.1
2000-10-01 | 3208.85 |  |  | 157.1
2000-09-30 | 3209.01 |  |  | 158.17
2000-09-29 | 3209.14 |  |  | 158.89
2000-09-28 | 3209.32 |  |  | 158.89
2000-09-27 | 3209.44 |  |  | 158.85
2000-09-26 | 3209.59 |  |  | 158.61
2000-09-25 | 3209.76 |  |  | 158.89
2000-09-24 | 3209.88 |  |  | 158.89
2000-09-23 | 3210.05 |  |  | 158.89
2000-09-22 | 3210.21 |  |  | 158.89
2000-09-21 | 3210.43 |  |  | 158.89
2000-09-20 | 3210.58 |  |  | 158.89
2000-09-19 | 3210.78 |  |  | 158.89
2000-09-18 | 3210.9 |  |  | 158.89
2000-09-17 | 3211.09 |  |  | 158.89
2000-09-16 | 3211.22 |  |  | 158.89
2000-09-15 | 3211.37 |  |  | 158.89
2000-09-14 | 3211.54 |  |  | 158.89
2000-09-13 | 3211.7 |  |  | 158.89
2000-09-12 | 3211.85 |  |  | 167.62
2000-09-11 | 3211.99 |  |  | 177.28
2000-09-10 | 3212.12 |  |  | 177.36
2000-09-09 | 3212.29 |  |  | 177.36
2000-09-08 | 3212.43 |  |  | 183.64
2000-09-07 | 3212.64 |  |  | 190.78
2000-09-06 | 3212.85 |  |  | 190.78
2000-09-05 | 3212.98 |  |  | 190.78
2000-09-04 | 3213.14 |  |  | 190.78
2000-09-03 | 3213.31 |  |  | 190.78
2000-09-02 | 3213.48 |  |  | 190.8
2000-09-01 | 3213.65 |  |  | 190.8
2000-08-31 | 3213.86 |  |  | 191.17
2000-08-30 | 3214.06 |  |  | 191.15
2000-08-29 | 3214.25 |  |  | 191.9
2000-08-28 | 3214.41 |  |  | 192.47
2000-08-27 | 3214.54 |  |  | 192.57
2000-08-26 | 3214.76 |  |  | 192.57
2000-08-25 | 3214.95 |  |  | 192.57
2000-08-24 | 3215.11 |  |  | 192.57
2000-08-23 | 3215.29 |  |  | 192.57
2000-08-22 | 3215.46 |  |  | 192.57
2000-08-21 | 3215.63 |  |  | 192.57
2000-08-20 | 3215.83 |  |  | 192.57
2000-08-19 | 3215.95 |  |  | 192.57
2000-08-18 | 3216.22 |  |  | 204.61
2000-08-17 | 3216.41 |  |  | 218.86
2000-08-16 | 3216.61 |  |  | 219.24
2000-08-15 | 3216.84 |  |  | 220.05
2000-08-14 | 3217.06 |  |  | 220.4
2000-08-13 | 3217.31 |  |  | 220.4
2000-08-12 | 3217.5 |  |  | 220.4
2000-08-11 | 3217.67 |  |  | 220.4
2000-08-10 | 3217.89 |  |  | 222.71
2000-08-09 | 3218.32 |  |  | 224.26
2000-08-08 | 3218.55 |  |  | 224.26
2000-08-07 | 3218.74 |  |  | 224.26
2000-08-06 | 3218.96 |  |  | 224.26
2000-08-05 | 3219.13 |  |  | 224.26
2000-08-04 | 3219.33 |  |  | 224.26
2000-08-03 | 3219.54 |  |  | 224.26
2000-08-02 | 3219.76 |  |  | 224.26
2000-08-01 | 3219.97 |  |  | 224.26
2000-07-31 | 3220.16 |  |  | 224.26
2000-07-30 | 3220.36 |  |  | 224.26
2000-07-29 | 3220.55 |  |  | 224.26
2000-07-28 | 3220.72 |  |  | 224.26
2000-07-27 | 3220.92 |  |  | 224.26
2000-07-26 | 3221.08 |  |  | 224.26
2000-07-25 | 3221.26 |  |  | 224.26
2000-07-24 | 3221.49 |  |  | 224.26
2000-07-23 | 3221.67 |  |  | 224.26
2000-07-22 | 3221.87 |  |  | 224.46
2000-07-21 | 3222.09 |  |  | 224.28
2000-07-20 | 3222.26 |  |  | 224.26
2000-07-19 | 3222.46 |  |  | 224.34
2000-07-18 | 3222.62 |  |  | 224.28
2000-07-17 | 3222.81 |  |  | 224.42
2000-07-16 | 3223.01 |  |  | 224.52
2000-07-15 | 3223.18 |  |  | 224.84
2000-07-14 | 3223.36 |  |  | 225.47
2000-07-13 | 3223.59 |  |  | 225.65
2000-07-12 | 3223.76 |  |  | 225.78
2000-07-11 | 3223.98 |  |  | 226.07
2000-07-10 | 3224.13 |  |  | 226.2
2000-07-09 | 3224.27 |  |  | 226.2
2000-07-08 | 3224.46 |  |  | 226.2
2000-07-07 | 3224.6 |  |  | 226.18
2000-07-06 | 3224.79 |  |  | 226.2
2000-07-05 | 3224.98 |  |  | 226.2
2000-07-04 | 3225.14 |  |  | 226.48
2000-07-03 | 3225.33 |  |  | 226.96
2000-07-02 | 3225.54 |  |  | 227.61
2000-07-01 | 3225.74 |  |  | 228.23
2000-06-30 | 3225.96 |  |  | 228.17
2000-06-29 | 3226.18 |  |  | 228.21
2000-06-28 | 3226.39 |  |  | 228.23
2000-06-27 | 3226.56 |  |  | 228.23
2000-06-26 | 3226.68 |  |  | 228.23
2000-06-25 | 3226.85 |  |  | 228.23
2000-06-24 | 3227.02 |  |  | 228.23
2000-06-23 | 3227.19 |  |  | 228.23
2000-06-22 | 3227.41 |  |  | 228.23
2000-06-21 | 3227.57 |  |  | 228.23
2000-06-20 | 3227.72 |  |  | 228.23
2000-06-19 | 3227.86 |  |  | 228.25
2000-06-18 | 3228.1 |  |  | 228.23
2000-06-17 | 3228.28 |  |  | 228.23
2000-06-16 | 3228.45 |  |  | 228.23
2000-06-15 | 3228.59 |  |  | 228.23
2000-06-14 | 3228.75 |  |  | 228.25
2000-06-13 | 3228.9 |  |  | 228.23
2000-06-12 | 3228.99 |  |  | 228.34
2000-06-11 | 3229.16 |  |  | 228.23
2000-06-10 | 3229.26 |  |  | 228.32
2000-06-09 | 3229.46 |  |  | 228.74
2000-06-08 | 3229.65 |  |  | 229.1
2000-06-07 | 3229.78 |  |  | 229.34
2000-06-06 | 3230 |  |  | 229.17
2000-06-05 | 3230.13 |  |  | 229.25
2000-06-04 | 3230.31 |  |  | 228.91
2000-06-03 | 3230.44 |  |  | 228.57
2000-06-02 | 3230.56 |  |  | 228.74
2000-06-01 | 3230.71 |  |  | 228.36
2000-05-31 | 3230.83 |  |  | 228.3
2000-05-30 | 3230.97 |  |  | 228.47
2000-05-29 | 3231.11 |  |  | 228.64
2000-05-28 | 3231.26 |  |  | 228.93
2000-05-27 | 3231.44 |  |  | 228.98
2000-05-26 | 3231.58 |  |  | 229.1
2000-05-25 | 3231.74 |  |  | 228.7
2000-05-24 | 3231.93 |  |  | 228.91
2000-05-23 | 3232.05 |  |  | 228.76
2000-05-22 | 3232.13 |  |  | 228.79
2000-05-21 | 3232.24 |  |  | 228.36
2000-05-20 | 3232.36 |  |  | 228.23
2000-05-19 | 3232.48 |  |  | 228.23
2000-05-18 | 3232.55 |  |  | 228.23
2000-05-17 | 3232.62 |  |  | 228.23
2000-05-16 | 3232.7 |  |  | 228.23
2000-05-15 | 3232.73 |  |  | 228.19
2000-05-14 | 3232.82 |  |  | 227.7
2000-05-13 | 3232.82 |  |  | 227.08
2000-05-12 | 3232.87 |  |  | 226.69
2000-05-11 | 3232.94 |  |  | 226.81
2000-05-10 | 3232.97 |  |  | 226.62
2000-05-09 | 3232.97 |  |  | 226.64
2000-05-08 | 3232.98 |  |  | 226.28
2000-05-07 | 3232.98 |  |  | 226.2
2000-05-06 | 3232.98 |  |  | 226.2
2000-05-05 | 3232.98 |  |  | 226.2
2000-05-04 | 3232.92 |  |  | 226
2000-05-03 | 3232.9 |  |  | 225.3
2000-05-02 | 3232.86 |  |  | 224.42
2000-05-01 | 3232.84 |  |  | 217.11
2000-04-30 | 3232.76 |  |  | 205.39
2000-04-29 | 3232.63 |  |  | 205.31
2000-04-28 | 3232.52 |  |  | 226.75
2000-04-27 | 3232.41 |  |  | 306.13
2000-04-26 | 3232.31 |  |  | 431.12
2000-04-25 | 3232.26 |  |  | 616.7
2000-04-24 | 3232.35 |  |  | 842.7
2000-04-23 | 3232.51 |  |  | 940.07
2000-04-22 | 3232.58 |  |  | 939.81
2000-04-21 | 3232.58 |  |  | 1168.02
2000-04-20 | 3232.73 |  |  | 1385.33
2000-04-19 | 3232.9 |  |  | 1385.33
2000-04-18 | 3232.9 |  |  | 1486.5
2000-04-17 | 3233.04 |  |  | 1761.15
2000-04-16 | 3234.04 |  |  | 1844.26
2000-04-15 | 3234.35 |  |  | 1845.14
2000-04-14 | 3234.5 |  |  | 1845.43
2000-04-13 | 3234.46 |  |  | 2048.04
2000-04-12 | 3234.04 |  |  | 2294.93
2000-04-11 | 3234.57 |  |  | 2326
2000-04-10 | 3235.1 |  |  | 2056.14
2000-04-09 | 3235.31 |  |  | 1328.94
2000-04-08 | 3235.2 |  |  | 472.44
2000-04-07 | 3234.61 |  |  | 918.63
2000-04-06 | 3234.13 |  |  | 581.79
2000-04-05 | 3233.31 |  |  | 1298.19
2000-04-04 | 3232.37 |  |  | 1773.08
2000-04-03 | 3231.83 |  |  | 1599.22
2000-04-02 | 3231.36 |  |  | 1508.03
2000-04-01 | 3231.25 |  |  | 1509.67
2000-03-31 | 3231.37 |  |  | 1510.38
2000-03-30 | 3231.68 |  |  | 1512.62
2000-03-29 | 3231.91 |  |  | 1516.09
2000-03-28 | 3231.91 |  |  | 1462.93
2000-03-27 | 3231.74 |  |  | 1355.76
2000-03-26 | 3231.45 |  |  | 1303.17
2000-03-25 | 3231.33 |  |  | 1303.17
2000-03-24 | 3231.26 |  |  | 1282.4
2000-03-23 | 3231.03 |  |  | 828.11
2000-03-22 | 3230.53 |  |  | 253.14
2000-03-21 | 3230.1 |  |  | 108.78
2000-03-20 | 3229.58 |  |  | 108.78
2000-03-19 | 3228.92 |  |  | 108.78
2000-03-18 | 3228.24 |  |  | 108.78
2000-03-17 | 3227.56 |  |  | 108.11
2000-03-16 | 3226.84 |  |  | 107.5
2000-03-15 | 3226.11 |  |  | 107.34
2000-03-14 | 3225.39 |  |  | 107.34
2000-03-13 | 3224.93 |  |  | 107.34
2000-03-12 | 3224.65 |  |  | 107.34
2000-03-11 | 3224.37 |  |  | 107.28
2000-03-10 | 3224.05 |  |  | 106.54
2000-03-09 | 3223.65 |  |  | 105.91
2000-03-08 | 3223.19 |  |  | 105.91
2000-03-07 | 3222.78 |  |  | 105.91
2000-03-06 | 3222.33 |  |  | 105.91
2000-03-05 | 3221.65 |  |  | 105.91
2000-03-04 | 3221.07 |  |  | 105.91
2000-03-03 | 3220.7 |  |  | 105.91
2000-03-02 | 3220.27 |  |  | 105.85
2000-03-01 | 3219.86 |  |  | 105.27
2000-02-29 | 3219.26 |  |  | 104.49
2000-02-28 | 3218.59 |  |  | 104.49
2000-02-27 | 3217.84 |  |  | 104.55
2000-02-26 | 3217.51 |  |  | 104.49
2000-02-25 | 3217.27 |  |  | 104.49
2000-02-24 | 3217.03 |  |  | 104.49
2000-02-23 | 3216.72 |  |  | 104.49
2000-02-22 | 3216.45 |  |  | 103.91
2000-02-21 | 3216.21 |  |  | 103.08
2000-02-20 | 3216.07 |  |  | 103.08
2000-02-19 | 3215.93 |  |  | 103.08
2000-02-18 | 3215.77 |  |  | 103.08
2000-02-17 | 3215.54 |  |  | 103.08
2000-02-16 | 3215.24 |  |  | 103.08
2000-02-15 | 3214.82 |  |  | 102.47
2000-02-14 | 3214.25 |  |  | 106.26
2000-02-13 | 3214.02 |  |  | 119.16
2000-02-12 | 3213.79 |  |  | 119.16
2000-02-11 | 3213.64 |  |  | 139.09
2000-02-10 | 3213.52 |  |  | 164.31
2000-02-09 | 3213.45 |  |  | 164.31
2000-02-08 | 3213.39 |  |  | 164.31
2000-02-07 | 3213.27 |  |  | 164.31
2000-02-06 | 3213.19 |  |  | 164.31
2000-02-05 | 3213.11 |  |  | 164.31
2000-02-04 | 3213.05 |  |  | 152.36
2000-02-03 | 3213.01 |  |  | 136.57
2000-02-02 | 3212.98 |  |  | 136.57
2000-02-01 | 3212.98 |  |  | 136.57
2000-01-31 | 3212.98 |  |  | 136.57
2000-01-30 | 3212.98 |  |  | 136.55
2000-01-29 | 3212.98 |  |  | 136.57
2000-01-28 | 3212.98 |  |  | 104.11
2000-01-27 | 3212.9 |  |  | 71.35
2000-01-26 | 3212.77 |  |  | 71.35
2000-01-25 | 3212.65 |  |  | 71.35
2000-01-24 | 3212.58 |  |  | 71.35
2000-01-23 | 3212.5 |  |  | 71.35
2000-01-22 | 3212.45 |  |  | 71.35
2000-01-21 | 3212.39 |  |  | 71.35
2000-01-20 | 3212.31 |  |  | 71.35
2000-01-19 | 3212.24 |  |  | 71.35
2000-01-18 | 3212.19 |  |  | 71.35
2000-01-17 | 3212.12 |  |  | 71.35
2000-01-16 | 3212.05 |  |  | 71.41
2000-01-15 | 3211.98 |  |  | 71.35
2000-01-14 | 3211.91 |  |  | 71.35
2000-01-13 | 3211.9 |  |  | 71.35
2000-01-12 | 3211.85 |  |  | 71.35
2000-01-11 | 3211.84 |  |  | 71.35
2000-01-10 | 3211.8 |  |  | 71.35
2000-01-09 | 3211.79 |  |  | 71.35
2000-01-08 | 3211.78 |  |  | 71.35
2000-01-07 | 3211.78 |  |  | 71.35
2000-01-06 | 3211.78 |  |  | 71.35
2000-01-05 | 3211.78 |  |  | 71.35
2000-01-04 | 3211.78 |  |  | 73.55
2000-01-03 | 3211.78 |  |  | 75.99
2000-01-02 | 3211.79 |  |  | 75.99
2000-01-01 | 3211.79 |  |  | 75.99
1999-12-31 | 3211.79 |  |  | 75.99
1999-12-30 | 3211.79 |  |  | 75.99
1999-12-29 | 3211.79 |  |  | 75.99
1999-12-28 | 3211.79 |  |  | 75.99
1999-12-27 | 3211.73 |  |  | 75.99
1999-12-26 | 3211.73 |  |  | 75.99
1999-12-25 | 3211.73 |  |  | 75.99
1999-12-24 | 3211.73 |  |  | 75.99
1999-12-23 | 3211.73 |  |  | 76.06
1999-12-22 | 3211.71 |  |  | 76.01
1999-12-21 | 3211.69 |  |  | 76.02
1999-12-20 | 3211.67 |  |  | 76.51
1999-12-19 | 3211.64 |  |  | 76.02
1999-12-18 | 3211.61 |  |  | 76.49
1999-12-17 | 3211.61 |  |  | 70.5
1999-12-16 | 3211.56 |  |  | 61.51
1999-12-15 | 3211.53 |  |  | 61.51
1999-12-14 | 3211.5 |  |  | 61.51
1999-12-13 | 3211.49 |  |  | 61.51
1999-12-12 | 3211.49 |  |  | 61.51
1999-12-11 | 3211.48 |  |  | 61.51
1999-12-10 | 3211.48 |  |  | 61.51
1999-12-09 | 3211.44 |  |  | 61.51
1999-12-08 | 3211.44 |  |  | 61.51
1999-12-07 | 3211.41 |  |  | 61.51
1999-12-06 | 3211.4 |  |  | 61.52
1999-12-05 | 3211.37 |  |  | 61.51
1999-12-04 | 3211.37 |  |  | 61.51
1999-12-03 | 3211.36 |  |  | 61.51
1999-12-02 | 3211.36 |  |  | 61.66
1999-12-01 | 3211.34 |  |  | 61.51
1999-11-30 | 3211.33 |  |  | 61.56
1999-11-29 | 3211.29 |  |  | 61.6
1999-11-28 | 3211.23 |  |  | 61.51
1999-11-27 | 3211.16 |  |  | 61.51
1999-11-26 | 3211.14 |  |  | 61.62
1999-11-25 | 3211.12 |  |  | 61.51
1999-11-24 | 3211.1 |  |  | 61.51
1999-11-23 | 3211.1 |  |  | 61.51
1999-11-22 | 3211.1 |  |  | 61.51
1999-11-21 | 3211.1 |  |  | 61.51
1999-11-20 | 3211.1 |  |  | 61.52
1999-11-19 | 3211.1 |  |  | 61.7
1999-11-18 | 3211.1 |  |  | 62.04
1999-11-17 | 3211.1 |  |  | 62.56
1999-11-16 | 3211.1 |  |  | 61.26
1999-11-15 | 3211.09 |  |  | 55.65
1999-11-14 | 3211.05 |  |  | 55.49
1999-11-13 | 3211.05 |  |  | 55.49
1999-11-12 | 3211.05 |  |  | 55.49
1999-11-11 | 3211.05 |  |  | 55.49
1999-11-10 | 3211.05 |  |  | 66.08
1999-11-09 | 3211.06 |  |  | 78.39
1999-11-08 | 3211.09 |  |  | 78.38
1999-11-07 | 3211.13 |  |  | 78.37
1999-11-06 | 3211.13 |  |  | 78.39
1999-11-05 | 3211.14 |  |  | 104.84
1999-11-04 | 3211.2 |  |  | 165.62
1999-11-03 | 3211.34 |  |  | 190.78
1999-11-02 | 3211.44 |  |  | 120.36
1999-11-01 | 3211.43 |  |  | 64.93
1999-10-31 | 3211.48 |  |  | 71.35
1999-10-30 | 3211.48 |  |  | 71.35
1999-10-29 | 3211.48 |  |  | 71.35
1999-10-28 | 3211.48 |  |  | 71.51
1999-10-27 | 3211.48 |  |  | 72.49
1999-10-26 | 3211.48 |  |  | 98.58
1999-10-25 | 3211.51 |  |  | 150.69
1999-10-24 | 3211.65 |  |  | 179.27
1999-10-23 | 3211.79 |  |  | 179.27
1999-10-22 | 3211.94 |  |  | 194.89
1999-10-21 | 3212.11 |  |  | 205.31
1999-10-20 | 3212.25 |  |  | 205.31
1999-10-19 | 3212.41 |  |  | 205.31
1999-10-18 | 3212.57 |  |  | 205.31
1999-10-17 | 3212.74 |  |  | 205.31
1999-10-16 | 3212.92 |  |  | 205.31
1999-10-15 | 3213.1 |  |  | 206.06
1999-10-14 | 3213.3 |  |  | 207.17
1999-10-13 | 3213.48 |  |  | 207.17
1999-10-12 | 3213.65 |  |  | 207.17
1999-10-11 | 3213.81 |  |  | 207.17
1999-10-10 | 3213.99 |  |  | 207.17
1999-10-09 | 3214.12 |  |  | 207.17
1999-10-08 | 3214.32 |  |  | 207.17
1999-10-07 | 3214.52 |  |  | 220.14
1999-10-06 | 3214.65 |  |  | 232.33
1999-10-05 | 3214.8 |  |  | 232.33
1999-10-04 | 3214.99 |  |  | 232.24
1999-10-03 | 3215.08 |  |  | 232.28
1999-10-02 | 3215.25 |  |  | 232.3
1999-10-01 | 3215.42 |  |  | 232.33
1999-09-30 | 3215.62 |  |  | 232.33
1999-09-29 | 3215.83 |  |  | 231.98
1999-09-28 | 3215.97 |  |  | 232.33
1999-09-27 | 3216.2 |  |  | 232.33
1999-09-26 | 3216.43 |  |  | 232.33
1999-09-25 | 3216.58 |  |  | 232.33
1999-09-24 | 3216.81 |  |  | 232.33
1999-09-23 | 3217.04 |  |  | 232.33
1999-09-22 | 3217.28 |  |  | 232.33
1999-09-21 | 3217.46 |  |  | 232.33
1999-09-20 | 3217.62 |  |  | 232.33
1999-09-19 | 3217.81 |  |  | 232.33
1999-09-18 | 3218 |  |  | 232.33
1999-09-17 | 3218.19 |  |  | 232.33
1999-09-16 | 3218.38 |  |  | 232.33
1999-09-15 | 3218.57 |  |  | 232.33
1999-09-14 | 3218.75 |  |  | 232.33
1999-09-13 | 3218.94 |  |  | 232.33
1999-09-12 | 3219.1 |  |  | 232.33
1999-09-11 | 3219.29 |  |  | 232.33
1999-09-10 | 3219.48 |  |  | 232.33
1999-09-09 | 3219.67 |  |  | 232.33
1999-09-08 | 3219.85 |  |  | 232.33
1999-09-07 | 3220.01 |  |  | 232.33
1999-09-06 | 3220.2 |  |  | 232.33
1999-09-05 | 3220.43 |  |  | 232.33
1999-09-04 | 3220.61 |  |  | 232.33
1999-09-03 | 3220.79 |  |  | 232.33
1999-09-02 | 3220.94 |  |  | 232.33
1999-09-01 | 3221.07 |  |  | 232.33
1999-08-31 | 3221.25 |  |  | 232.33
1999-08-30 | 3221.45 |  |  | 232.33
1999-08-29 | 3221.67 |  |  | 232.33
1999-08-28 | 3221.88 |  |  | 232.33
1999-08-27 | 3222.05 |  |  | 232.33
1999-08-26 | 3222.23 |  |  | 232.33
1999-08-25 | 3222.4 |  |  | 232.33
1999-08-24 | 3222.56 |  |  | 232.33
1999-08-23 | 3222.67 |  |  | 232.35
1999-08-22 | 3222.9 |  |  | 232.33
1999-08-21 | 3223.06 |  |  | 232.33
1999-08-20 | 3223.24 |  |  | 232.33
1999-08-19 | 3223.42 |  |  | 232.33
1999-08-18 | 3223.75 |  |  | 229.66
1999-08-17 | 3223.9 |  |  | 228.23
1999-08-16 | 3224.05 |  |  | 228.23
1999-08-15 | 3224.19 |  |  | 228.23
1999-08-14 | 3224.36 |  |  | 228.23
1999-08-13 | 3224.53 |  |  | 228.23
1999-08-12 | 3224.69 |  |  | 228.23
1999-08-11 | 3224.89 |  |  | 228.23
1999-08-10 | 3225.05 |  |  | 228.23
1999-08-09 | 3225.21 |  |  | 228.23
1999-08-08 | 3225.4 |  |  | 228.23
1999-08-07 | 3225.58 |  |  | 228.23
1999-08-06 | 3225.73 |  |  | 228.23
1999-08-05 | 3225.87 |  |  | 228.56
1999-08-04 | 3226.05 |  |  | 228.23
1999-08-03 | 3226.2 |  |  | 228.23
1999-08-02 | 3226.4 |  |  | 228.23
1999-08-01 | 3226.56 |  |  | 228.23
1999-07-31 | 3226.72 |  |  | 228.23
1999-07-30 | 3226.9 |  |  | 228.23
1999-07-29 | 3227.09 |  |  | 228.23
1999-07-28 | 3227.27 |  |  | 228.23
1999-07-27 | 3227.43 |  |  | 228.23
1999-07-26 | 3227.58 |  |  | 228.23
1999-07-25 | 3227.73 |  |  | 228.23
1999-07-24 | 3227.89 |  |  | 228.23
1999-07-23 | 3228.08 |  |  | 228.25
1999-07-22 | 3228.23 |  |  | 228.23
1999-07-21 | 3228.38 |  |  | 228.23
1999-07-20 | 3228.54 |  |  | 228.32
1999-07-19 | 3228.69 |  |  | 228.38
1999-07-18 | 3228.82 |  |  | 228.36
1999-07-17 | 3228.99 |  |  | 228.85
1999-07-16 | 3229.2 |  |  | 229.13
1999-07-15 | 3229.38 |  |  | 229.2
1999-07-14 | 3229.55 |  |  | 229.91
1999-07-13 | 3229.79 |  |  | 230.06
1999-07-12 | 3229.92 |  |  | 230.15
1999-07-11 | 3230.11 |  |  | 230.25
1999-07-10 | 3230.24 |  |  | 230.27
1999-07-09 | 3230.37 |  |  | 230.27
1999-07-08 | 3230.48 |  |  | 230.27
1999-07-07 | 3230.62 |  |  | 230.27
1999-07-06 | 3230.81 |  |  | 230.3
1999-07-05 | 3230.96 |  |  | 230.3
1999-07-04 | 3231.05 |  |  | 230.27
1999-07-03 | 3231.15 |  |  | 230.38
1999-07-02 | 3231.35 |  |  | 230.68
1999-07-01 | 3231.54 |  |  | 231.07
1999-06-30 | 3231.68 |  |  | 236.86
1999-06-29 | 3231.86 |  |  | 242.73
1999-06-28 | 3231.98 |  |  | 242.73
1999-06-27 | 3232.13 |  |  | 242.73
1999-06-26 | 3232.23 |  |  | 242.73
1999-06-25 | 3232.39 |  |  | 242.73
1999-06-24 | 3232.58 |  |  | 243.02
1999-06-23 | 3232.72 |  |  | 242.73
1999-06-22 | 3232.87 |  |  | 242.73
1999-06-21 | 3232.99 |  |  | 242.73
1999-06-20 | 3233.16 |  |  | 242.8
1999-06-19 | 3233.28 |  |  | 242.8
1999-06-18 | 3233.39 |  |  | 243.21
1999-06-17 | 3233.53 |  |  | 242.86
1999-06-16 | 3233.65 |  |  | 243.02
1999-06-15 | 3233.78 |  |  | 242.91
1999-06-14 | 3233.9 |  |  | 242.75
1999-06-13 | 3233.97 |  |  | 242.73
1999-06-12 | 3234.01 |  |  | 242.73
1999-06-11 | 3234.09 |  |  | 242.73
1999-06-10 | 3234.17 |  |  | 242.66
1999-06-09 | 3234.21 |  |  | 242.64
1999-06-08 | 3234.26 |  |  | 242.36
1999-06-07 | 3234.29 |  |  | 242.06
1999-06-06 | 3234.31 |  |  | 242.12
1999-06-05 | 3234.31 |  |  | 242.04
1999-06-04 | 3234.31 |  |  | 241.57
1999-06-03 | 3234.27 |  |  | 240.96
1999-06-02 | 3234.2 |  |  | 240.78
1999-06-01 | 3234.19 |  |  | 240.83
1999-05-31 | 3234.17 |  |  | 240.78
1999-05-30 | 3234.01 |  |  | 240.4
1999-05-29 | 3233.9 |  |  | 239.8
1999-05-28 | 3233.76 |  |  | 239.28
1999-05-27 | 3233.55 |  |  | 238.65
1999-05-26 | 3233.28 |  |  | 238.39
1999-05-25 | 3232.91 |  |  | 225.57
1999-05-24 | 3232.6 |  |  | 239.75
1999-05-23 | 3232.19 |  |  | 259.5
1999-05-22 | 3231.83 |  |  | 258.26
1999-05-21 | 3231.43 |  |  | 257.75
1999-05-20 | 3231.05 |  |  | 257.71
1999-05-19 | 3230.7 |  |  | 257.71
1999-05-18 | 3230.39 |  |  | 315.96
1999-05-17 | 3230.13 |  |  | 479.92
1999-05-16 | 3229.94 |  |  | 582.95
1999-05-15 | 3229.89 |  |  | 582.95
1999-05-14 | 3229.82 |  |  | 582.95
1999-05-13 | 3229.69 |  |  | 582.95
1999-05-12 | 3229.55 |  |  | 687.54
1999-05-11 | 3229.49 |  |  | 810.5
1999-05-10 | 3229.49 |  |  | 1047.69
1999-05-09 | 3229.65 |  |  | 1252.38
1999-05-08 | 3229.78 |  |  | 1252.97
1999-05-07 | 3229.78 |  |  | 1343.76
1999-05-06 | 3229.93 |  |  | 1470.58
1999-05-05 | 3230.23 |  |  | 1470.42
1999-05-04 | 3230.42 |  |  | 1476.44
1999-05-03 | 3230.51 |  |  | 1478.72
1999-05-02 | 3230.52 |  |  | 1478.72
1999-05-01 | 3230.56 |  |  | 1478.72
1999-04-30 | 3230.62 |  |  | 1478.3
1999-04-29 | 3230.81 |  |  | 1478.64
1999-04-28 | 3230.84 |  |  | 1478.39
1999-04-27 | 3230.77 |  |  | 1478.18
1999-04-26 | 3230.5 |  |  | 1037.44
1999-04-25 | 3229.68 |  |  | 643.94
1999-04-24 | 3228.47 |  |  | 640.8
1999-04-23 | 3227.47 |  |  | 637.77
1999-04-22 | 3226.61 |  |  | 636.02
1999-04-21 | 3225.5 |  |  | 632.32
1999-04-20 | 3223.98 |  |  | 628.49
1999-04-19 | 3222.01 |  |  | 622.54
1999-04-18 | 3219.93 |  |  | 617.43
1999-04-17 | 3217.75 |  |  | 612.24
1999-04-16 | 3216.01 |  |  | 608.15
1999-04-15 | 3214.13 |  |  | 604.97
1999-04-14 | 3213.62 |  |  | 603.18
1999-04-13 | 3212.74 |  |  | 600.29
1999-04-12 | 3212.13 |  |  | 599.24
1999-04-11 | 3211.75 |  |  | 599.15
1999-04-10 | 3211.5 |  |  | 598.36
1999-04-09 | 3211.12 |  |  | 595.52
1999-04-08 | 3210.6 |  |  | 595.14
1999-04-07 | 3210.09 |  |  | 594.37
1999-04-06 | 3209.83 |  |  | 826.75
1999-04-05 | 3209.93 |  |  | 1202.68
1999-04-04 | 3210.19 |  |  | 1470.75
1999-04-03 | 3210.76 |  |  | 1475.19
1999-04-02 | 3211.18 |  |  | 1683.19
1999-04-01 | 3211.86 |  |  | 2398.26
1999-03-31 | 3213.08 |  |  | 2882.9
1999-03-30 | 3214.62 |  |  | 2901.14
1999-03-29 | 3215.97 |  |  | 2917.8
1999-03-28 | 3217.13 |  |  | 2931.13
1999-03-27 | 3217.97 |  |  | 2937.36
1999-03-26 | 3218.04 |  |  | 2750.6
1999-03-25 | 3217.36 |  |  | 2264.61
1999-03-24 | 3216.28 |  |  | 1867.69
1999-03-23 | 3215.31 |  |  | 1236.87
1999-03-22 | 3214.1 |  |  | 724.81
1999-03-21 | 3211.63 |  |  | 493.71
1999-03-20 | 3209.11 |  |  | 488.86
1999-03-19 | 3207.75 |  |  | 487.97
1999-03-18 | 3207.01 |  |  | 485.38
1999-03-17 | 3206.28 |  |  | 485.38
1999-03-16 | 3205.66 |  |  | 485.34
1999-03-15 | 3205.03 |  |  | 483.73
1999-03-14 | 3204.72 |  |  | 482.67
1999-03-13 | 3204.66 |  |  | 483.59
1999-03-12 | 3204.65 |  |  | 485.38
1999-03-11 | 3204.65 |  |  | 485.38
1999-03-10 | 3204.65 |  |  | 485.38
1999-03-09 | 3204.62 |  |  | 780.62
1999-03-08 | 3204.88 |  |  | 1772.89
1999-03-07 | 3205.99 |  |  | 2450.62
1999-03-06 | 3207.73 |  |  | 2469.62
1999-03-05 | 3209.42 |  |  | 2488.52
1999-03-04 | 3210.96 |  |  | 2505.18
1999-03-03 | 3212.28 |  |  | 2517.02
1999-03-02 | 3213.35 |  |  | 2518.17
1999-03-01 | 3213.83 |  |  | 1226.35
1999-02-28 | 3212.17 |  |  | 300.75
1999-02-27 | 3211.02 |  |  | 257.13
1999-02-26 | 3210.52 |  |  | 255.79
1999-02-25 | 3209.82 |  |  | 255.39
1999-02-24 | 3209.02 |  |  | 254.5
1999-02-23 | 3208.5 |  |  | 253.58
1999-02-22 | 3208.47 |  |  | 253.38
1999-02-21 | 3208.41 |  |  | 253.38
1999-02-20 | 3208.39 |  |  | 253.42
1999-02-19 | 3208.28 |  |  | 271.23
1999-02-18 | 3208.26 |  |  | 300.07
1999-02-17 | 3208.26 |  |  | 299.55
1999-02-16 | 3208.26 |  |  | 299.86
1999-02-15 | 3208.32 |  |  | 299.81
1999-02-14 | 3208.42 |  |  | 299.41
1999-02-13 | 3208.44 |  |  | 299.46
1999-02-12 | 3208.45 |  |  | 361
1999-02-11 | 3208.68 |  |  | 406.69
1999-02-10 | 3208.94 |  |  | 406.69
1999-02-09 | 3209.12 |  |  | 406.69
1999-02-08 | 3209.26 |  |  | 406.81
1999-02-07 | 3209.33 |  |  | 406.81
1999-02-06 | 3209.47 |  |  | 407.53
1999-02-05 | 3209.66 |  |  | 407.02
1999-02-04 | 3209.85 |  |  | 406.8
1999-02-03 | 3210.01 |  |  | 407.04
1999-02-02 | 3210.14 |  |  | 407.52
1999-02-01 | 3210.34 |  |  | 407.63
1999-01-31 | 3210.52 |  |  | 408.09
1999-01-30 | 3210.67 |  |  | 407.93
1999-01-29 | 3210.81 |  |  | 408.81
1999-01-28 | 3210.94 |  |  | 409.02
1999-01-27 | 3211.08 |  |  | 409.1
1999-01-26 | 3211.19 |  |  | 409.63
1999-01-25 | 3211.41 |  |  | 409.56
1999-01-24 | 3211.47 |  |  | 409.75
1999-01-23 | 3211.47 |  |  | 409.75
1999-01-22 | 3211.47 |  |  | 346.66
1999-01-21 | 3211.26 |  |  | 304.22
1999-01-20 | 3211.05 |  |  | 303.57
1999-01-19 | 3210.72 |  |  | 302.48
1999-01-18 | 3210.46 |  |  | 301.97
1999-01-17 | 3210.33 |  |  | 301.95
1999-01-16 | 3210.21 |  |  | 301.85
1999-01-15 | 3210.24 |  |  | 301.85
1999-01-14 | 3210.34 |  |  | 301.85
1999-01-13 | 3210.45 |  |  | 301.85
1999-01-12 | 3210.5 |  |  | 301.85
1999-01-11 | 3210.6 |  |  | 301.85
1999-01-10 | 3210.69 |  |  | 301.85
1999-01-09 | 3210.77 |  |  | 301.85
1999-01-08 | 3210.87 |  |  | 301.85
1999-01-07 | 3210.95 |  |  | 301.85
1999-01-06 | 3211.01 |  |  | 301.85
1999-01-05 | 3211.02 |  |  | 301.85
1999-01-04 | 3211.02 |  |  | 301.85
1999-01-03 | 3211.01 |  |  | 301.85
1999-01-02 | 3210.98 |  |  | 299.83
1999-01-01 | 3210.75 |  |  | 299.41
1998-12-31 | 3210.39 |  |  | 261.15
1998-12-30 | 3209.94 |  |  | 219.49
1998-12-29 | 3209.28 |  |  | 218.48
1998-12-28 | 3208.86 |  |  | 218.48
1998-12-27 | 3208.86 |  |  | 218.48
1998-12-26 | 3208.93 |  |  | 218.48
1998-12-25 | 3208.98 |  |  | 218.48
1998-12-24 | 3209.06 |  |  | 218.48
1998-12-23 | 3209.21 |  |  | 218.48
1998-12-22 | 3209.33 |  |  | 218.48
1998-12-21 | 3209.46 |  |  | 218.5
1998-12-20 | 3209.65 |  |  | 218.6
1998-12-19 | 3209.77 |  |  | 219.64
1998-12-18 | 3209.77 |  |  | 219.92
1998-12-17 | 3209.73 |  |  | 220.28
1998-12-16 | 3209.67 |  |  | 220.08
1998-12-15 | 3209.58 |  |  | 219.03
1998-12-14 | 3209.26 |  |  | 218.48
1998-12-13 | 3209.06 |  |  | 218.74
1998-12-12 | 3209.06 |  |  | 218.82
1998-12-11 | 3209.06 |  |  | 243.54
1998-12-10 | 3209.18 |  |  | 320.31
1998-12-09 | 3209.38 |  |  | 425.97
1998-12-08 | 3209.67 |  |  | 498.56
1998-12-07 | 3209.95 |  |  | 532.24
1998-12-06 | 3210.29 |  |  | 532.59
1998-12-05 | 3210.6 |  |  | 532.59
1998-12-04 | 3210.87 |  |  | 505.34
1998-12-03 | 3210.92 |  |  | 438.85
1998-12-02 | 3210.91 |  |  | 340.63
1998-12-01 | 3210.83 |  |  | 232.82
1998-11-30 | 3210.72 |  |  | 111.85
1998-11-29 | 3210.55 |  |  | 80.92
1998-11-28 | 3210.38 |  |  | 80.79
1998-11-27 | 3210.15 |  |  | 80.79
1998-11-26 | 3209.98 |  |  | 80.82
1998-11-25 | 3209.79 |  |  | 80.93
1998-11-24 | 3209.53 |  |  | 80.79
1998-11-23 | 3209.21 |  |  | 80.78
1998-11-22 | 3209 |  |  | 80.79
1998-11-21 | 3208.67 |  |  | 80.78
1998-11-20 | 3208.62 |  |  | 88.07
1998-11-19 | 3208.58 |  |  | 98.93
1998-11-18 | 3208.58 |  |  | 98.93
1998-11-17 | 3208.58 |  |  | 98.93
1998-11-16 | 3208.58 |  |  | 77.92
1998-11-15 | 3208.56 |  |  | 84.79
1998-11-14 | 3208.58 |  |  | 101.69
1998-11-13 | 3208.58 |  |  | 101.69
1998-11-12 | 3208.58 |  |  | 101.69
1998-11-11 | 3208.58 |  |  | 101.69
1998-11-10 | 3208.58 |  |  | 101.67
1998-11-09 | 3208.58 |  |  | 101.61
1998-11-08 | 3208.6 |  |  | 101.67
1998-11-07 | 3208.6 |  |  | 101.54
1998-11-06 | 3208.6 |  |  | 101.15
1998-11-05 | 3208.6 |  |  | 91.84
1998-11-04 | 3208.58 |  |  | 96.21
1998-11-03 | 3208.58 |  |  | 95.97
1998-11-02 | 3208.58 |  |  | 80.64
1998-11-01 | 3208.57 |  |  | 67.98
1998-10-31 | 3208.57 |  |  | 89.7
1998-10-30 | 3208.64 |  |  | 128.49
1998-10-29 | 3208.68 |  |  | 128.49
1998-10-28 | 3208.75 |  |  | 128.5
1998-10-27 | 3208.77 |  |  | 178.17
1998-10-26 | 3208.88 |  |  | 273.87
1998-10-25 | 3209.09 |  |  | 329.8
1998-10-24 | 3209.36 |  |  | 329.8
1998-10-23 | 3209.63 |  |  | 329.8
1998-10-22 | 3209.92 |  |  | 329.8
1998-10-21 | 3210.13 |  |  | 329.8
1998-10-20 | 3210.43 |  |  | 329.8
1998-10-19 | 3210.7 |  |  | 329.8
1998-10-18 | 3210.99 |  |  | 329.8
1998-10-17 | 3211.23 |  |  | 329.8
1998-10-16 | 3211.5 |  |  | 329.8
1998-10-15 | 3211.77 |  |  | 329.8
1998-10-14 | 3212.05 |  |  | 329.8
1998-10-13 | 3212.31 |  |  | 329.8
1998-10-12 | 3212.57 |  |  | 329.91
1998-10-11 | 3212.86 |  |  | 329.83
1998-10-10 | 3213.13 |  |  | 329.96
1998-10-09 | 3213.4 |  |  | 330.95
1998-10-08 | 3213.69 |  |  | 332
1998-10-07 | 3214.01 |  |  | 332.14
1998-10-06 | 3214.28 |  |  | 332.7
1998-10-05 | 3214.56 |  |  | 332.51
1998-10-04 | 3214.76 |  |  | 333.01
1998-10-03 | 3215.04 |  |  | 334.12
1998-10-02 | 3215.34 |  |  | 335.07
1998-10-01 | 3215.62 |  |  | 335.12
1998-09-30 | 3215.94 |  |  | 335.12
1998-09-29 | 3216.17 |  |  | 335.15
1998-09-28 | 3216.55 |  |  | 335.53
1998-09-27 | 3216.77 |  |  | 336.14
1998-09-26 | 3217.03 |  |  | 337.08
1998-09-25 | 3217.3 |  |  | 337.77
1998-09-24 | 3217.62 |  |  | 337.77
1998-09-23 | 3217.91 |  |  | 291.75
1998-09-22 | 3218.12 |  |  | 246.96
1998-09-21 | 3218.31 |  |  | 246.96
1998-09-20 | 3218.52 |  |  | 246.96
1998-09-19 | 3218.71 |  |  | 246.96
1998-09-18 | 3218.93 |  |  | 247.09
1998-09-17 | 3219.18 |  |  | 247.16
1998-09-16 | 3219.43 |  |  | 247.18
1998-09-15 | 3219.63 |  |  | 246.96
1998-09-14 | 3219.83 |  |  | 246.98
1998-09-13 | 3220.02 |  |  | 247
1998-09-12 | 3220.19 |  |  | 247.16
1998-09-11 | 3220.38 |  |  | 234.59
1998-09-10 | 3220.58 |  |  | 226.2
1998-09-09 | 3220.77 |  |  | 226.2
1998-09-08 | 3221 |  |  | 226.22
1998-09-07 | 3221.2 |  |  | 226.2
1998-09-06 | 3221.35 |  |  | 226.2
1998-09-05 | 3221.54 |  |  | 226.2
1998-09-04 | 3221.72 |  |  | 226.2
1998-09-03 | 3221.92 |  |  | 226.39
1998-09-02 | 3222.1 |  |  | 226.43
1998-09-01 | 3222.28 |  |  | 226.26
1998-08-31 | 3222.43 |  |  | 226.33
1998-08-30 | 3222.61 |  |  | 226.45
1998-08-29 | 3222.79 |  |  | 226.39
1998-08-28 | 3222.97 |  |  | 226.52
1998-08-27 | 3223.16 |  |  | 226.56
1998-08-26 | 3223.35 |  |  | 226.96
1998-08-25 | 3223.49 |  |  | 226.94
1998-08-24 | 3223.65 |  |  | 226.67
1998-08-23 | 3223.82 |  |  | 226.56
1998-08-22 | 3224 |  |  | 226.63
1998-08-21 | 3224.19 |  |  | 226.77
1998-08-20 | 3224.36 |  |  | 226.52
1998-08-19 | 3224.51 |  |  | 226.86
1998-08-18 | 3224.7 |  |  | 226.99
1998-08-17 | 3224.89 |  |  | 227.57
1998-08-16 | 3225.08 |  |  | 228.03
1998-08-15 | 3225.3 |  |  | 228.23
1998-08-14 | 3225.51 |  |  | 228.21
1998-08-13 | 3225.7 |  |  | 228.23
1998-08-12 | 3225.85 |  |  | 228.21
1998-08-11 | 3226.02 |  |  | 228.23
1998-08-10 | 3226.19 |  |  | 228.19
1998-08-09 | 3226.39 |  |  | 228.21
1998-08-08 | 3226.56 |  |  | 227.85
1998-08-07 | 3226.74 |  |  | 227.88
1998-08-06 | 3226.89 |  |  | 227.84
1998-08-05 | 3227.07 |  |  | 227.51
1998-08-04 | 3227.26 |  |  | 227.27
1998-08-03 | 3227.38 |  |  | 227.07
1998-08-02 | 3227.53 |  |  | 226.88
1998-08-01 | 3227.64 |  |  | 227.11
1998-07-31 | 3227.77 |  |  | 227.09
1998-07-30 | 3227.9 |  |  | 227.45
1998-07-29 | 3228.08 |  |  | 226.92
1998-07-28 | 3228.22 |  |  | 227
1998-07-27 | 3228.4 |  |  | 227
1998-07-26 | 3228.55 |  |  | 226.92
1998-07-25 | 3228.71 |  |  | 226.73
1998-07-24 | 3228.83 |  |  | 227
1998-07-23 | 3229.01 |  |  | 226.43
1998-07-22 | 3229.16 |  |  | 226.6
1998-07-21 | 3229.33 |  |  | 226.5
1998-07-20 | 3229.42 |  |  | 226.43
1998-07-19 | 3229.6 |  |  | 226.2
1998-07-18 | 3229.74 |  |  | 226.2
1998-07-17 | 3229.87 |  |  | 224.5
1998-07-16 | 3230.07 |  |  | 222.32
1998-07-15 | 3230.13 |  |  | 222.32
1998-07-14 | 3230.22 |  |  | 237.09
1998-07-13 | 3230.35 |  |  | 243.64
1998-07-12 | 3230.47 |  |  | 243.37
1998-07-11 | 3230.59 |  |  | 243.19
1998-07-10 | 3230.72 |  |  | 243.6
1998-07-09 | 3230.88 |  |  | 244.84
1998-07-08 | 3230.96 |  |  | 244.84
1998-07-07 | 3231.03 |  |  | 244.72
1998-07-06 | 3231.1 |  |  | 244.14
1998-07-05 | 3231.18 |  |  | 243.72
1998-07-04 | 3231.28 |  |  | 243.04
1998-07-03 | 3231.31 |  |  | 242.75
1998-07-02 | 3231.32 |  |  | 242.73
1998-07-01 | 3231.32 |  |  | 242.75
1998-06-30 | 3231.34 |  |  | 242.73
1998-06-29 | 3231.45 |  |  | 242.73
1998-06-28 | 3231.5 |  |  | 242.73
1998-06-27 | 3231.53 |  |  | 242.73
1998-06-26 | 3231.56 |  |  | 242.73
1998-06-25 | 3231.57 |  |  | 269.95
1998-06-24 | 3231.63 |  |  | 309.22
1998-06-23 | 3231.71 |  |  | 309.22
1998-06-22 | 3231.83 |  |  | 309.22
1998-06-21 | 3231.91 |  |  | 309.22
1998-06-20 | 3232.01 |  |  | 309.22
1998-06-19 | 3232.08 |  |  | 309.22
1998-06-18 | 3232.14 |  |  | 340.9
1998-06-17 | 3232.21 |  |  | 468.53
1998-06-16 | 3232.35 |  |  | 621.72
1998-06-15 | 3232.61 |  |  | 845.52
1998-06-14 | 3232.98 |  |  | 1006.06
1998-06-13 | 3233.36 |  |  | 1310.81
1998-06-12 | 3233.82 |  |  | 1887.66
1998-06-11 | 3234.61 |  |  | 2079.1
1998-06-10 | 3235.55 |  |  | 2134.59
1998-06-09 | 3236.47 |  |  | 2243.22
1998-06-08 | 3237.41 |  |  | 2166.84
1998-06-07 | 3238.29 |  |  | 2126.31
1998-06-06 | 3239.14 |  |  | 2093.17
1998-06-05 | 3239.87 |  |  | 1958.42
1998-06-04 | 3240.43 |  |  | 2096.27
1998-06-03 | 3240.96 |  |  | 2015.29
1998-06-02 | 3241.27 |  |  | 1989.88
1998-06-01 | 3241.27 |  |  | 1963.92
1998-05-31 | 3240.87 |  |  | 1730.81
1998-05-30 | 3239.28 |  |  | 1406.32
1998-05-29 | 3236.56 |  |  | 1312.73
1998-05-28 | 3235.55 |  |  | 1295.88
1998-05-27 | 3235.68 |  |  | 1360.57
1998-05-26 | 3235.68 |  |  | 1127.74
1998-05-25 | 3235.6 |  |  | 732.09
1998-05-24 | 3235.59 |  |  | 733.32
1998-05-23 | 3235.7 |  |  | 742.74
1998-05-22 | 3235.77 |  |  | 740.47
1998-05-21 | 3235.77 |  |  | 702.98
1998-05-20 | 3235.76 |  |  | 703.2
1998-05-19 | 3235.74 |  |  | 700.3
1998-05-18 | 3235.71 |  |  | 695.21
1998-05-17 | 3235.6 |  |  | 683.24
1998-05-16 | 3235.46 |  |  | 676.47
1998-05-15 | 3235.46 |  |  | 676.25
1998-05-14 | 3235.47 |  |  | 676.39
1998-05-13 | 3235.42 |  |  | 670.93
1998-05-12 | 3235.31 |  |  | 718.42
1998-05-11 | 3235.39 |  |  | 839.61
1998-05-10 | 3235.57 |  |  | 917.48
1998-05-09 | 3235.69 |  |  | 923.33
1998-05-08 | 3235.74 |  |  | 1037.94
1998-05-07 | 3235.92 |  |  | 1168.63
1998-05-06 | 3235.95 |  |  | 1172.31
1998-05-05 | 3235.96 |  |  | 1030.82
1998-05-04 | 3235.93 |  |  | 933.96
1998-05-03 | 3235.75 |  |  | 923.07
1998-05-02 | 3235.65 |  |  | 911.57
1998-05-01 | 3235.55 |  |  | 899.99
1998-04-30 | 3235.37 |  |  | 961.28
1998-04-29 | 3235.2 |  |  | 999.9
1998-04-28 | 3235.06 |  |  | 1288.62
1998-04-27 | 3235.24 |  |  | 1663.99
1998-04-26 | 3235.61 |  |  | 1826.72
1998-04-25 | 3235.96 |  |  | 1855.51
1998-04-24 | 3236.08 |  |  | 1619.93
1998-04-23 | 3235.88 |  |  | 1486.8
1998-04-22 | 3235.81 |  |  | 1205.11
1998-04-21 | 3235.64 |  |  | 885.08
1998-04-20 | 3235.46 |  |  | 463.81
1998-04-19 | 3235.15 |  |  | 205.12
1998-04-18 | 3234.81 |  |  | 203.77
1998-04-17 | 3234.54 |  |  | 203.47
1998-04-16 | 3234.23 |  |  | 203.47
1998-04-15 | 3233.87 |  |  | 203.47
1998-04-14 | 3233.55 |  |  | 203.51
1998-04-13 | 3233.16 |  |  | 203.47
1998-04-12 | 3232.83 |  |  | 202.88
1998-04-11 | 3232.44 |  |  | 202.16
1998-04-10 | 3232 |  |  | 222.43
1998-04-09 | 3231.62 |  |  | 276.5
1998-04-08 | 3231.3 |  |  | 387.99
1998-04-07 | 3231 |  |  | 522.61
1998-04-06 | 3230.75 |  |  | 636.58
1998-04-05 | 3230.52 |  |  | 698.88
1998-04-04 | 3230.23 |  |  | 698.26
1998-04-03 | 3229.93 |  |  | 762.41
1998-04-02 | 3229.88 |  |  | 1056.42
1998-04-01 | 3230.08 |  |  | 1271.48
1998-03-31 | 3230.17 |  |  | 1626.25
1998-03-30 | 3230.55 |  |  | 2006.7
1998-03-29 | 3231.2 |  |  | 2047.13
1998-03-28 | 3231.89 |  |  | 2050.47
1998-03-27 | 3232.32 |  |  | 2041.79
1998-03-26 | 3232.29 |  |  | 2026.11
1998-03-25 | 3231.91 |  |  | 2026.32
1998-03-24 | 3230.87 |  |  | 1549.01
1998-03-23 | 3228.09 |  |  | 621.5
1998-03-22 | 3224.35 |  |  | 197.9
1998-03-21 | 3221.81 |  |  | 196.61
1998-03-20 | 3220.72 |  |  | 196.15
1998-03-19 | 3219.9 |  |  | 195.33
1998-03-18 | 3219.1 |  |  | 194.38
1998-03-17 | 3218.18 |  |  | 194.36
1998-03-16 | 3217.01 |  |  | 193.51
1998-03-15 | 3215.78 |  |  | 192.57
1998-03-14 | 3214.09 |  |  | 191.76
1998-03-13 | 3214.03 |  |  | 190.78
1998-03-12 | 3213.51 |  |  | 203.58
1998-03-11 | 3213.39 |  |  | 288.57
1998-03-10 | 3213.47 |  |  | 327.18
1998-03-09 | 3213.51 |  |  | 327.15
1998-03-08 | 3213.52 |  |  | 327.15
1998-03-07 | 3213.52 |  |  | 327.15
1998-03-06 | 3213.52 |  |  | 327.15
1998-03-05 | 3213.43 |  |  | 327.15
1998-03-04 | 3213.34 |  |  | 327.15
1998-03-03 | 3213.14 |  |  | 327.15
1998-03-02 | 3213.09 |  |  | 327.18
1998-03-01 | 3213.16 |  |  | 327.15
1998-02-28 | 3213.27 |  |  | 310.78
1998-02-27 | 3213.38 |  |  | 275.62
1998-02-26 | 3213.44 |  |  | 275.62
1998-02-25 | 3213.44 |  |  | 275.62
1998-02-24 | 3213.44 |  |  | 275.62
1998-02-23 | 3213.44 |  |  | 275.6
1998-02-22 | 3213.42 |  |  | 275.62
1998-02-21 | 3213.35 |  |  | 275.65
1998-02-20 | 3213.35 |  |  | 296.73
1998-02-19 | 3213.45 |  |  | 327.15
1998-02-18 | 3213.56 |  |  | 327.15
1998-02-17 | 3213.62 |  |  | 327.15
1998-02-16 | 3213.7 |  |  | 327.18
1998-02-15 | 3213.72 |  |  | 327.15
1998-02-14 | 3213.74 |  |  | 327.15
1998-02-13 | 3213.77 |  |  | 327.15
1998-02-12 | 3213.8 |  |  | 308.35
1998-02-11 | 3213.73 |  |  | 280.29
1998-02-10 | 3213.69 |  |  | 280.29
1998-02-09 | 3213.61 |  |  | 280.29
1998-02-08 | 3213.42 |  |  | 280.29
1998-02-07 | 3213.18 |  |  | 280.29
1998-02-06 | 3212.9 |  |  | 261.14
1998-02-05 | 3212.69 |  |  | 237.16
1998-02-04 | 3212.4 |  |  | 236.52
1998-02-03 | 3212.19 |  |  | 236.5
1998-02-02 | 3212.16 |  |  | 236.48
1998-02-01 | 3212.13 |  |  | 236.72
1998-01-31 | 3212.03 |  |  | 216.74
1998-01-30 | 3211.85 |  |  | 194.36
1998-01-29 | 3211.57 |  |  | 137.66
1998-01-28 | 3211.16 |  |  | 69.09
1998-01-27 | 3210.53 |  |  | 69.09
1998-01-26 | 3210.05 |  |  | 68.91
1998-01-25 | 3209.84 |  |  | 68.37
1998-01-24 | 3209.6 |  |  | 68.16
1998-01-23 | 3209.32 |  |  | 68.2
1998-01-22 | 3209.15 |  |  | 67.98
1998-01-21 | 3208.93 |  |  | 68.1
1998-01-20 | 3208.65 |  |  | 67.98
1998-01-19 | 3208.22 |  |  | 67.98
1998-01-18 | 3207.73 |  |  | 67.98
1998-01-17 | 3207.31 |  |  | 67.98
1998-01-16 | 3207.13 |  |  | 67.94
1998-01-15 | 3207.03 |  |  | 67.8
1998-01-14 | 3206.99 |  |  | 67.74
1998-01-13 | 3206.95 |  |  | 66.98
1998-01-12 | 3206.95 |  |  | 67.21
1998-01-11 | 3206.95 |  |  | 67.64
1998-01-10 | 3206.95 |  |  | 67.03
1998-01-09 | 3206.95 |  |  | 67.28
1998-01-08 | 3206.95 |  |  | 67.35
1998-01-07 | 3206.95 |  |  | 67.1
1998-01-06 | 3206.95 |  |  | 67.72
1998-01-05 | 3206.96 |  |  | 67.21
1998-01-04 | 3206.96 |  |  | 66.89
1998-01-03 | 3206.96 |  |  | 67.33
1998-01-02 | 3206.96 |  |  | 67.67
1998-01-01 | 3206.96 |  |  | 67.59
1997-12-31 | 3206.96 |  |  | 66.87
1997-12-30 | 3206.95 |  |  | 66.94
1997-12-29 | 3206.95 |  |  | 66.87
1997-12-28 | 3206.95 |  |  | 66.87
1997-12-27 | 3206.95 |  |  | 66.87
1997-12-26 | 3206.95 |  |  | 66.87
1997-12-25 | 3206.95 |  |  | 66.87
1997-12-24 | 3207 |  |  | 66.89
1997-12-23 | 3206.97 |  |  | 66.9
1997-12-22 | 3206.97 |  |  | 67.05
1997-12-21 | 3206.97 |  |  | 67.55
1997-12-20 | 3206.97 |  |  | 67.53
1997-12-19 | 3206.97 |  |  | 67.53
1997-12-18 | 3206.92 |  |  | 67.98
1997-12-17 | 3206.92 |  |  | 67.98
1997-12-16 | 3206.92 |  |  | 67.91
1997-12-15 | 3206.92 |  |  | 67.97
1997-12-14 | 3206.92 |  |  | 67.75
1997-12-13 | 3206.92 |  |  | 67.81
1997-12-12 | 3206.93 |  |  | 67.98
1997-12-11 | 3207.05 |  |  | 68.24
1997-12-10 | 3207.05 |  |  | 68.73
1997-12-09 | 3207.05 |  |  | 69.09
1997-12-08 | 3207.05 |  |  | 69.09
1997-12-07 | 3207.05 |  |  | 69.06
1997-12-06 | 3207.05 |  |  | 69.09
1997-12-05 | 3207.05 |  |  | 69.07
1997-12-04 | 3207.06 |  |  | 69.06
1997-12-03 | 3207.06 |  |  | 69.06
1997-12-02 | 3207.06 |  |  | 69.09
1997-12-01 | 3207.06 |  |  | 69.09
1997-11-30 | 3207.06 |  |  | 69.09
1997-11-29 | 3207.06 |  |  | 69.09
1997-11-28 | 3207.06 |  |  | 69.09
1997-11-27 | 3207.06 |  |  | 69.09
1997-11-26 | 3207.06 |  |  | 69.09
1997-11-25 | 3207.06 |  |  | 69.09
1997-11-24 | 3207.06 |  |  | 70.23
1997-11-23 | 3207.06 |  |  | 77.18
1997-11-22 | 3207.06 |  |  | 77.17
1997-11-21 | 3207.06 |  |  | 82.1
1997-11-20 | 3207.25 |  |  | 88.46
1997-11-19 | 3207.25 |  |  | 89.27
1997-11-18 | 3207.26 |  |  | 89.21
1997-11-17 | 3207.26 |  |  | 89.6
1997-11-16 | 3207.27 |  |  | 89.5
1997-11-15 | 3207.27 |  |  | 89.48
1997-11-14 | 3207.27 |  |  | 89.57
1997-11-13 | 3207.27 |  |  | 89.6
1997-11-12 | 3207.27 |  |  | 89.6
1997-11-11 | 3207.32 |  |  | 89.6
1997-11-10 | 3207.32 |  |  | 89.6
1997-11-09 | 3207.32 |  |  | 89.6
1997-11-08 | 3207.32 |  |  | 89.6
1997-11-07 | 3207.32 |  |  | 89.6
1997-11-06 | 3207.32 |  |  | 78.97
1997-11-05 | 3207.4 |  |  | 96.21
1997-11-04 | 3207.45 |  |  | 96.21
1997-11-03 | 3207.45 |  |  | 96.21
1997-11-02 | 3207.46 |  |  | 96.21
1997-11-01 | 3207.47 |  |  | 96.21
1997-10-31 | 3207.47 |  |  | 103.05
1997-10-30 | 3207.47 |  |  | 113.18
1997-10-29 | 3207.52 |  |  | 113.16
1997-10-28 | 3207.52 |  |  | 113.16
1997-10-27 | 3207.66 |  |  | 113.16
1997-10-26 | 3207.66 |  |  | 113.16
1997-10-25 | 3207.67 |  |  | 113.16
1997-10-24 | 3207.67 |  |  | 116.9
1997-10-23 | 3207.82 |  |  | 122.73
1997-10-22 | 3207.91 |  |  | 122.81
1997-10-21 | 3207.96 |  |  | 122.99
1997-10-20 | 3208.01 |  |  | 123.4
1997-10-19 | 3208.09 |  |  | 123.59
1997-10-18 | 3208.15 |  |  | 123.74
1997-10-17 | 3208.21 |  |  | 123.78
1997-10-16 | 3208.29 |  |  | 123.44
1997-10-15 | 3208.36 |  |  | 122.91
1997-10-14 | 3208.41 |  |  | 122.79
1997-10-13 | 3208.48 |  |  | 122.61
1997-10-12 | 3208.5 |  |  | 122.24
1997-10-11 | 3208.57 |  |  | 122.39
1997-10-10 | 3208.63 |  |  | 121.95
1997-10-09 | 3208.76 |  |  | 120.69
1997-10-08 | 3208.82 |  |  | 120.71
1997-10-07 | 3208.94 |  |  | 120.69
1997-10-06 | 3209.02 |  |  | 120.69
1997-10-05 | 3209.16 |  |  | 120.69
1997-10-04 | 3209.24 |  |  | 120.69
1997-10-03 | 3209.42 |  |  | 120.69
1997-10-02 | 3209.51 |  |  | 120.69
1997-10-01 | 3209.62 |  |  | 133.8
1997-09-30 | 3209.81 |  |  | 146.63
1997-09-29 | 3209.97 |  |  | 146.63
1997-09-28 | 3210.09 |  |  | 146.63
1997-09-27 | 3210.28 |  |  | 146.75
1997-09-26 | 3210.37 |  |  | 158.65
1997-09-25 | 3210.57 |  |  | 173.57
1997-09-24 | 3210.69 |  |  | 173.57
1997-09-23 | 3210.77 |  |  | 173.57
1997-09-22 | 3210.96 |  |  | 173.57
1997-09-21 | 3211.09 |  |  | 173.57
1997-09-20 | 3211.24 |  |  | 173.57
1997-09-19 | 3211.32 |  |  | 188.87
1997-09-18 | 3211.5 |  |  | 212.79
1997-09-17 | 3211.64 |  |  | 209.4
1997-09-16 | 3211.84 |  |  | 207.17
1997-09-15 | 3211.97 |  |  | 207.19
1997-09-14 | 3212.19 |  |  | 207.19
1997-09-13 | 3212.44 |  |  | 207.31
1997-09-12 | 3212.59 |  |  | 207.4
1997-09-11 | 3212.82 |  |  | 207.79
1997-09-10 | 3213.12 |  |  | 207.65
1997-09-09 | 3213.31 |  |  | 207.44
1997-09-08 | 3213.51 |  |  | 207.52
1997-09-07 | 3213.68 |  |  | 207.31
1997-09-06 | 3213.87 |  |  | 207.32
1997-09-05 | 3213.99 |  |  | 207.46
1997-09-04 | 3214.24 |  |  | 207.19
1997-09-03 | 3214.4 |  |  | 207.23
1997-09-02 | 3214.53 |  |  | 207.21
1997-09-01 | 3214.66 |  |  | 207.17
1997-08-31 | 3214.85 |  |  | 207.16
1997-08-30 | 3215.01 |  |  | 206.98
1997-08-29 | 3215.22 |  |  | 206.98
1997-08-28 | 3215.44 |  |  | 206.67
1997-08-27 | 3215.65 |  |  | 206.47
1997-08-26 | 3215.91 |  |  | 206.55
1997-08-25 | 3216.1 |  |  | 207.67
1997-08-24 | 3216.3 |  |  | 210.06
1997-08-23 | 3216.46 |  |  | 209.84
1997-08-22 | 3216.6 |  |  | 209.91
1997-08-21 | 3216.87 |  |  | 210.52
1997-08-20 | 3217.05 |  |  | 210.89
1997-08-19 | 3217.23 |  |  | 210.87
1997-08-18 | 3217.4 |  |  | 210.91
1997-08-17 | 3217.6 |  |  | 210.85
1997-08-16 | 3217.79 |  |  | 210.75
1997-08-15 | 3217.98 |  |  | 210.91
1997-08-14 | 3218.19 |  |  | 210.89
1997-08-13 | 3218.4 |  |  | 210.54
1997-08-12 | 3218.65 |  |  | 210.91
1997-08-11 | 3218.91 |  |  | 210.91
1997-08-10 | 3219.07 |  |  | 210.91
1997-08-09 | 3219.26 |  |  | 210.91
1997-08-08 | 3219.47 |  |  | 210.91
1997-08-07 | 3219.71 |  |  | 210.91
1997-08-06 | 3219.92 |  |  | 210.91
1997-08-05 | 3220.07 |  |  | 210.91
1997-08-04 | 3220.22 |  |  | 210.91
1997-08-03 | 3220.37 |  |  | 210.91
1997-08-02 | 3220.49 |  |  | 210.91
1997-08-01 | 3220.66 |  |  | 210.91
1997-07-31 | 3220.78 |  |  | 210.93
1997-07-30 | 3220.93 |  |  | 210.91
1997-07-29 | 3220.99 |  |  | 211.22
1997-07-28 | 3221.13 |  |  | 211.12
1997-07-27 | 3221.37 |  |  | 211.04
1997-07-26 | 3221.57 |  |  | 211.12
1997-07-25 | 3221.79 |  |  | 211.36
1997-07-24 | 3221.99 |  |  | 211.51
1997-07-23 | 3222.18 |  |  | 211.59
1997-07-22 | 3222.39 |  |  | 211.63
1997-07-21 | 3222.54 |  |  | 211.75
1997-07-20 | 3222.74 |  |  | 211.73
1997-07-19 | 3222.88 |  |  | 211.65
1997-07-18 | 3223.05 |  |  | 211.98
1997-07-17 | 3223.2 |  |  | 211.94
1997-07-16 | 3223.38 |  |  | 211.9
1997-07-15 | 3223.52 |  |  | 211.77
1997-07-14 | 3223.67 |  |  | 211.67
1997-07-13 | 3223.85 |  |  | 211.74
1997-07-12 | 3223.99 |  |  | 211.65
1997-07-11 | 3224.13 |  |  | 211.81
1997-07-10 | 3224.37 |  |  | 211.79
1997-07-09 | 3224.47 |  |  | 212.07
1997-07-08 | 3224.73 |  |  | 212.03
1997-07-07 | 3224.91 |  |  | 211.87
1997-07-06 | 3225.12 |  |  | 211.89
1997-07-05 | 3225.25 |  |  | 211.95
1997-07-04 | 3225.42 |  |  | 211.81
1997-07-03 | 3225.52 |  |  | 211.61
1997-07-02 | 3225.68 |  |  | 215.1
1997-07-01 | 3225.78 |  |  | 230.83
1997-06-30 | 3225.84 |  |  | 260.05
1997-06-29 | 3225.94 |  |  | 294.04
1997-06-28 | 3226.17 |  |  | 293.86
1997-06-27 | 3226.33 |  |  | 293.89
1997-06-26 | 3226.51 |  |  | 294.3
1997-06-25 | 3226.69 |  |  | 294.2
1997-06-24 | 3226.87 |  |  | 294.21
1997-06-23 | 3227.01 |  |  | 294.44
1997-06-22 | 3227.22 |  |  | 294.49
1997-06-21 | 3227.47 |  |  | 282.87
1997-06-20 | 3227.67 |  |  | 280.2
1997-06-19 | 3227.92 |  |  | 280.27
1997-06-18 | 3228.12 |  |  | 280.29
1997-06-17 | 3228.28 |  |  | 280.34
1997-06-16 | 3228.5 |  |  | 280.29
1997-06-15 | 3228.62 |  |  | 280.29
1997-06-14 | 3228.74 |  |  | 280.27
1997-06-13 | 3228.82 |  |  | 280.22
1997-06-12 | 3228.85 |  |  | 327.29
1997-06-11 | 3229.09 |  |  | 361.42
1997-06-10 | 3229.21 |  |  | 361.05
1997-06-09 | 3229.46 |  |  | 361.46
1997-06-08 | 3229.63 |  |  | 361.74
1997-06-07 | 3229.89 |  |  | 361.63
1997-06-06 | 3230.03 |  |  | 361.82
1997-06-05 | 3230.17 |  |  | 337.8
1997-06-04 | 3230.4 |  |  | 311.7
1997-06-03 | 3230.56 |  |  | 311.91
1997-06-02 | 3230.68 |  |  | 311.76
1997-06-01 | 3230.82 |  |  | 311.91
1997-05-31 | 3230.94 |  |  | 312.41
1997-05-30 | 3231.19 |  |  | 312.04
1997-05-29 | 3231.33 |  |  | 311.7
1997-05-28 | 3231.73 |  |  | 311.94
1997-05-27 | 3231.86 |  |  | 312.04
1997-05-26 | 3232 |  |  | 311.86
1997-05-25 | 3232.12 |  |  | 311.96
1997-05-24 | 3232.26 |  |  | 311.99
1997-05-23 | 3232.4 |  |  | 312.22
1997-05-22 | 3232.6 |  |  | 312.28
1997-05-21 | 3232.77 |  |  | 312.2
1997-05-20 | 3232.95 |  |  | 312.12
1997-05-19 | 3233.13 |  |  | 312.02
1997-05-18 | 3233.32 |  |  | 311.76
1997-05-17 | 3233.51 |  |  | 312.09
1997-05-16 | 3233.65 |  |  | 279.72
1997-05-15 | 3233.72 |  |  | 253.36
1997-05-14 | 3233.72 |  |  | 252.71
1997-05-13 | 3233.72 |  |  | 287.9
1997-05-12 | 3233.76 |  |  | 312.81
1997-05-11 | 3233.76 |  |  | 312.04
1997-05-10 | 3233.76 |  |  | 311.7
1997-05-09 | 3233.76 |  |  | 311.7
1997-05-08 | 3233.76 |  |  | 311.7
1997-05-07 | 3233.76 |  |  | 338.87
1997-05-06 | 3233.73 |  |  | 369.71
1997-05-05 | 3233.73 |  |  | 368.84
1997-05-04 | 3233.72 |  |  | 368.13
1997-05-03 | 3233.72 |  |  | 526.9
1997-05-02 | 3233.72 |  |  | 681.76
1997-05-01 | 3233.83 |  |  | 947.1
1997-04-30 | 3234.16 |  |  | 1216.43
1997-04-29 | 3234.46 |  |  | 1394.61
1997-04-28 | 3234.76 |  |  | 1719.12
1997-04-27 | 3235.26 |  |  | 1851.32
1997-04-26 | 3235.87 |  |  | 1898.61
1997-04-25 | 3236.5 |  |  | 1951.43
1997-04-24 | 3236.72 |  |  | 1602.98
1997-04-23 | 3236.5 |  |  | 1184.69
1997-04-22 | 3236.26 |  |  | 1160.89
1997-04-21 | 3236.14 |  |  | 951.17
1997-04-20 | 3235.85 |  |  | 695.05
1997-04-19 | 3235.32 |  |  | 667.69
1997-04-18 | 3235.31 |  |  | 662.84
1997-04-17 | 3235.37 |  |  | 663.3
1997-04-16 | 3235.39 |  |  | 667.36
1997-04-15 | 3235.46 |  |  | 599.86
1997-04-14 | 3235.43 |  |  | 466.03
1997-04-13 | 3235.27 |  |  | 326.02
1997-04-12 | 3235.24 |  |  | 322.13
1997-04-11 | 3235.11 |  |  | 315.48
1997-04-10 | 3234.93 |  |  | 312.32
1997-04-09 | 3234.83 |  |  | 309.22
1997-04-08 | 3234.65 |  |  | 309.17
1997-04-07 | 3234.47 |  |  | 308.1
1997-04-06 | 3234.3 |  |  | 306.99
1997-04-05 | 3234.12 |  |  | 306.75
1997-04-04 | 3233.92 |  |  | 306.75
1997-04-03 | 3233.72 |  |  | 390.21
1997-04-02 | 3233.58 |  |  | 550.97
1997-04-01 | 3233.52 |  |  | 758.03
1997-03-31 | 3233.52 |  |  | 969.89
1997-03-30 | 3233.52 |  |  | 1091.42
1997-03-29 | 3233.45 |  |  | 1091.35
1997-03-28 | 3233.34 |  |  | 1090.88
1997-03-27 | 3233.07 |  |  | 1088.84
1997-03-26 | 3232.65 |  |  | 446.21
1997-03-25 | 3231.8 |  |  | 145.38
1997-03-24 | 3230.81 |  |  | 144.14
1997-03-23 | 3229.71 |  |  | 143.23
1997-03-22 | 3228.48 |  |  | 142.54
1997-03-21 | 3227.1 |  |  | 141.55
1997-03-20 | 3225.58 |  |  | 141.59
1997-03-19 | 3224.32 |  |  | 141.55
1997-03-18 | 3223.26 |  |  | 141.32
1997-03-17 | 3222.33 |  |  | 140.06
1997-03-16 | 3221.48 |  |  | 139.88
1997-03-15 | 3220.97 |  |  | 139.6
1997-03-14 | 3220.56 |  |  | 138.3
1997-03-13 | 3220.1 |  |  | 138.22
1997-03-12 | 3219.53 |  |  | 138.22
1997-03-11 | 3218.79 |  |  | 137.56
1997-03-10 | 3217.99 |  |  | 136.62
1997-03-09 | 3217.66 |  |  | 136.57
1997-03-08 | 3217.31 |  |  | 136.57
1997-03-07 | 3216.97 |  |  | 136.57
1997-03-06 | 3216.66 |  |  | 136.57
1997-03-05 | 3216.36 |  |  | 136.57
1997-03-04 | 3216.06 |  |  | 135.49
1997-03-03 | 3215.73 |  |  | 135.1
1997-03-02 | 3215.25 |  |  | 134.97
1997-03-01 | 3214.9 |  |  | 135
1997-02-28 | 3214.67 |  |  | 180.14
1997-02-27 | 3214.12 |  |  | 242.73
1997-02-26 | 3214.12 |  |  | 242.73
1997-02-25 | 3214 |  |  | 346.11
1997-02-24 | 3213.98 |  |  | 546.3
1997-02-23 | 3214.11 |  |  | 649.88
1997-02-22 | 3214.24 |  |  | 652.01
1997-02-21 | 3214.24 |  |  | 684.23
1997-02-20 | 3214.12 |  |  | 708.2
1997-02-19 | 3214.12 |  |  | 708.25
1997-02-18 | 3214.03 |  |  | 708.2
1997-02-17 | 3213.81 |  |  | 708.2
1997-02-16 | 3213.81 |  |  | 708.2
1997-02-15 | 3213.87 |  |  | 708.2
1997-02-14 | 3214.02 |  |  | 708.2
1997-02-13 | 3214.18 |  |  | 708.2
1997-02-12 | 3214.46 |  |  | 759.13
1997-02-11 | 3214.67 |  |  | 815.67
1997-02-10 | 3214.97 |  |  | 815.67
1997-02-09 | 3215.14 |  |  | 815.67
1997-02-08 | 3215.34 |  |  | 815.67
1997-02-07 | 3215.53 |  |  | 909.28
1997-02-06 | 3215.79 |  |  | 1023.8
1997-02-05 | 3216.08 |  |  | 1024.88
1997-02-04 | 3216.1 |  |  | 1026.78
1997-02-03 | 3216.01 |  |  | 1020.99
1997-02-02 | 3214.12 |  |  | 1016.84
1997-02-01 | 3214.12 |  |  | 1010.39
1997-01-31 | 3212.98 |  |  | 597.74
1997-01-30 | 3212.01 |  |  | 480.2
1997-01-29 | 3211.49 |  |  | 478.49
1997-01-28 | 3210.66 |  |  | 478.45
1997-01-27 | 3210.66 |  |  | 478.45
1997-01-26 | 3210.73 |  |  | 478.45
1997-01-25 | 3210.85 |  |  | 478.45
1997-01-24 | 3211.04 |  |  | 529.5
1997-01-23 | 3211.29 |  |  | 640.32
1997-01-22 | 3211.6 |  |  | 698.98
1997-01-21 | 3211.88 |  |  | 699.12
1997-01-20 | 3212.14 |  |  | 699.08
1997-01-19 | 3212.29 |  |  | 699.08
1997-01-18 | 3212.33 |  |  | 699.75
1997-01-17 | 3212.39 |  |  | 659.12
1997-01-16 | 3212.52 |  |  | 595.14
1997-01-15 | 3212.73 |  |  | 595.14
1997-01-14 | 3213.06 |  |  | 806.13
1997-01-13 | 3213.58 |  |  | 1233.54
1997-01-12 | 3214.37 |  |  | 1430.85
1997-01-11 | 3215.03 |  |  | 1432.56
1997-01-10 | 3215.6 |  |  | 1437.17
1997-01-09 | 3216.14 |  |  | 1675.43
1997-01-08 | 3216.93 |  |  | 2185.84
1997-01-07 | 3218 |  |  | 2698.84
1997-01-06 | 3219.45 |  |  | 2932.31
1997-01-05 | 3220.99 |  |  | 2946.72
1997-01-04 | 3222.12 |  |  | 2957.57
1997-01-03 | 3222.46 |  |  | 2957.85
1997-01-02 | 3221.47 |  |  | 2941.04
1997-01-01 | 3218.45 |  |  | 2911.81
1996-12-31 | 3215.15 |  |  | 2491.42
1996-12-30 | 3212.84 |  |  | 1508.25
1996-12-29 | 3211.15 |  |  | 1018.33
1996-12-28 | 3210.8 |  |  | 661.4
1996-12-27 | 3209.91 |  |  | 325.75
1996-12-26 | 3208.37 |  |  | 146.63
1996-12-25 | 3207.89 |  |  | 146.63
1996-12-24 | 3207.72 |  |  | 146.63
1996-12-23 | 3207.62 |  |  | 168.27
1996-12-22 | 3207.55 |  |  | 197.98
1996-12-21 | 3207.5 |  |  | 197.98
1996-12-20 | 3207.46 |  |  | 197.98
1996-12-19 | 3207.46 |  |  | 334.09
1996-12-18 | 3207.63 |  |  | 741.87
1996-12-17 | 3208.15 |  |  | 1240.16
1996-12-16 | 3209.02 |  |  | 1767.92
1996-12-15 | 3210.35 |  |  | 2043.65
1996-12-14 | 3211.93 |  |  | 2057.83
1996-12-13 | 3213.32 |  |  | 2069.81
1996-12-12 | 3214.51 |  |  | 2084.49
1996-12-11 | 3215.32 |  |  | 1611.97
1996-12-10 | 3214.94 |  |  | 823.49
1996-12-09 | 3213.67 |  |  | 365.79
1996-12-08 | 3212.88 |  |  | 236.46
1996-12-07 | 3212.71 |  |  | 236.44
1996-12-06 | 3212.67 |  |  | 236.46
1996-12-05 | 3212.72 |  |  | 236.46
1996-12-04 | 3212.73 |  |  | 236.42
1996-12-03 | 3212.84 |  |  | 236.46
1996-12-02 | 3212.9 |  |  | 236.46
1996-12-01 | 3212.92 |  |  | 236.46
1996-11-30 | 3212.98 |  |  | 236.46
1996-11-29 | 3213.06 |  |  | 236.46
1996-11-28 | 3213.1 |  |  | 236.48
1996-11-27 | 3213.13 |  |  | 236.46
1996-11-26 | 3213.2 |  |  | 236.46
1996-11-25 | 3213.21 |  |  | 236.46
1996-11-24 | 3213.22 |  |  | 236.48
1996-11-23 | 3213.22 |  |  | 236.46
1996-11-22 | 3213.22 |  |  | 236.46
1996-11-21 | 3213.17 |  |  | 236.63
1996-11-20 | 3213.1 |  |  | 236.53
1996-11-19 | 3212.85 |  |  | 193.46
1996-11-18 | 3212.71 |  |  | 135.43
1996-11-17 | 3212.69 |  |  | 134.93
1996-11-16 | 3212.76 |  |  | 134.93
1996-11-15 | 3212.81 |  |  | 134.97
1996-11-14 | 3212.84 |  |  | 134.93
1996-11-13 | 3212.89 |  |  | 134.93
1996-11-12 | 3212.91 |  |  | 134.93
1996-11-11 | 3212.98 |  |  | 134.93
1996-11-10 | 3213.05 |  |  | 134.93
1996-11-09 | 3213.1 |  |  | 134.93
1996-11-08 | 3213.1 |  |  | 111.47
1996-11-07 | 3213.08 |  |  | 77.2
1996-11-06 | 3213.08 |  |  | 77.33
1996-11-05 | 3213.08 |  |  | 77.59
1996-11-04 | 3213.08 |  |  | 78.35
1996-11-03 | 3213.08 |  |  | 78.37
1996-11-02 | 3213.08 |  |  | 78.12
1996-11-01 | 3213.06 |  |  | 77.44
1996-10-31 | 3213.06 |  |  | 77.41
1996-10-30 | 3213.06 |  |  | 77.23
1996-10-29 | 3213.06 |  |  | 69.39
1996-10-28 | 3213.06 |  |  | 82.02
1996-10-27 | 3213.06 |  |  | 82.02
1996-10-26 | 3213.06 |  |  | 82.02
1996-10-25 | 3213.06 |  |  | 82.02
1996-10-24 | 3213.06 |  |  | 82.02
1996-10-23 | 3213.07 |  |  | 82.02
1996-10-22 | 3213.07 |  |  | 87.94
1996-10-21 | 3213.12 |  |  | 107.73
1996-10-20 | 3213.2 |  |  | 123.78
1996-10-19 | 3213.26 |  |  | 123.78
1996-10-18 | 3213.32 |  |  | 134.07
1996-10-17 | 3213.38 |  |  | 161.89
1996-10-16 | 3213.52 |  |  | 179.25
1996-10-15 | 3213.65 |  |  | 179.23
1996-10-14 | 3213.78 |  |  | 179.27
1996-10-13 | 3213.94 |  |  | 179.27
1996-10-12 | 3214.07 |  |  | 179.27
1996-10-11 | 3214.19 |  |  | 179.27
1996-10-10 | 3214.37 |  |  | 179.27
1996-10-09 | 3214.49 |  |  | 169.98
1996-10-08 | 3214.55 |  |  | 162.49
1996-10-07 | 3214.61 |  |  | 162.49
1996-10-06 | 3214.78 |  |  | 162.49
1996-10-05 | 3214.89 |  |  | 162.49
1996-10-04 | 3215.01 |  |  | 162.49
1996-10-03 | 3215.13 |  |  | 162.38
1996-10-02 | 3215.23 |  |  | 161.54
1996-10-01 | 3215.33 |  |  | 161.23
1996-09-30 | 3215.45 |  |  | 160.98
1996-09-29 | 3215.61 |  |  | 160.7
1996-09-28 | 3215.74 |  |  | 160.68
1996-09-27 | 3215.85 |  |  | 160.68
1996-09-26 | 3215.93 |  |  | 160.68
1996-09-25 | 3216.02 |  |  | 160.68
1996-09-24 | 3216.19 |  |  | 160.68
1996-09-23 | 3216.33 |  |  | 160.68
1996-09-22 | 3216.44 |  |  | 160.68
1996-09-21 | 3216.55 |  |  | 160.68
1996-09-20 | 3216.7 |  |  | 175.9
1996-09-19 | 3216.85 |  |  | 198.28
1996-09-18 | 3216.99 |  |  | 216.47
1996-09-17 | 3217.2 |  |  | 234.39
1996-09-16 | 3217.36 |  |  | 234.39
1996-09-15 | 3217.61 |  |  | 234.47
1996-09-14 | 3217.8 |  |  | 234.41
1996-09-13 | 3218 |  |  | 234.6
1996-09-12 | 3218.18 |  |  | 234.5
1996-09-11 | 3218.41 |  |  | 234.39
1996-09-10 | 3218.59 |  |  | 234.45
1996-09-09 | 3218.78 |  |  | 234.39
1996-09-08 | 3218.97 |  |  | 234.54
1996-09-07 | 3219.19 |  |  | 234.97
1996-09-06 | 3219.36 |  |  | 235.06
1996-09-05 | 3219.54 |  |  | 235.78
1996-09-04 | 3219.76 |  |  | 236.23
1996-09-03 | 3220 |  |  | 236.35
1996-09-02 | 3220.21 |  |  | 236.46
1996-09-01 | 3220.46 |  |  | 236.46
1996-08-31 | 3220.67 |  |  | 236.46
1996-08-30 | 3220.88 |  |  | 236.46
1996-08-29 | 3221.11 |  |  | 236.46
1996-08-28 | 3221.28 |  |  | 236.46
1996-08-27 | 3221.47 |  |  | 236.48
1996-08-26 | 3221.62 |  |  | 236.46
1996-08-25 | 3221.84 |  |  | 236.46
1996-08-24 | 3222.03 |  |  | 236.46
1996-08-23 | 3222.21 |  |  | 236.46
1996-08-22 | 3222.4 |  |  | 236.46
1996-08-21 | 3222.6 |  |  | 236.46
1996-08-20 | 3222.81 |  |  | 236.48
1996-08-19 | 3223 |  |  | 236.46
1996-08-18 | 3223.21 |  |  | 236.46
1996-08-17 | 3223.45 |  |  | 226.3
1996-08-16 | 3223.66 |  |  | 207.17
1996-08-15 | 3223.87 |  |  | 210.14
1996-08-14 | 3224 |  |  | 231.94
1996-08-13 | 3224.22 |  |  | 240.65
1996-08-12 | 3224.35 |  |  | 240.63
1996-08-11 | 3224.56 |  |  | 240.63
1996-08-10 | 3224.77 |  |  | 240.65
1996-08-09 | 3224.94 |  |  | 240.63
1996-08-08 | 3225.12 |  |  | 240.63
1996-08-07 | 3225.28 |  |  | 240.63
1996-08-06 | 3225.46 |  |  | 240.63
1996-08-05 | 3225.63 |  |  | 240.63
1996-08-04 | 3225.87 |  |  | 240.63
1996-08-03 | 3226.06 |  |  | 240.86
1996-08-02 | 3226.27 |  |  | 242.73
1996-08-01 | 3226.54 |  |  | 242.73
1996-07-31 | 3226.77 |  |  | 242.73
1996-07-30 | 3226.96 |  |  | 242.73
1996-07-29 | 3227.14 |  |  | 242.73
1996-07-28 | 3227.31 |  |  | 242.73
1996-07-27 | 3227.46 |  |  | 242.73
1996-07-26 | 3227.64 |  |  | 242.73
1996-07-25 | 3227.83 |  |  | 242.73
1996-07-24 | 3228.01 |  |  | 242.73
1996-07-23 | 3228.19 |  |  | 242.73
1996-07-22 | 3228.34 |  |  | 242.73
1996-07-21 | 3228.48 |  |  | 242.73
1996-07-20 | 3228.63 |  |  | 242.73
1996-07-19 | 3228.79 |  |  | 242.73
1996-07-18 | 3228.99 |  |  | 242.95
1996-07-17 | 3229.18 |  |  | 240.89
1996-07-16 | 3229.42 |  |  | 242.3
1996-07-15 | 3229.65 |  |  | 242.73
1996-07-14 | 3229.81 |  |  | 242.73
1996-07-13 | 3230.02 |  |  | 242.73
1996-07-12 | 3230.17 |  |  | 242.73
1996-07-11 | 3230.3 |  |  | 242.73
1996-07-10 | 3230.44 |  |  | 242.73
1996-07-09 | 3230.58 |  |  | 242.73
1996-07-08 | 3230.78 |  |  | 242.73
1996-07-07 | 3230.9 |  |  | 242.73
1996-07-06 | 3231.04 |  |  | 242.73
1996-07-05 | 3231.18 |  |  | 242.73
1996-07-04 | 3231.39 |  |  | 242.73
1996-07-03 | 3231.56 |  |  | 242.73
1996-07-02 | 3231.74 |  |  | 242.73
1996-07-01 | 3231.85 |  |  | 242.73
1996-06-30 | 3231.93 |  |  | 250.96
1996-06-29 | 3232.04 |  |  | 255.74
1996-06-28 | 3232.15 |  |  | 255.67
1996-06-27 | 3232.33 |  |  | 255.63
1996-06-26 | 3232.44 |  |  | 255.72
1996-06-25 | 3232.53 |  |  | 255.58
1996-06-24 | 3232.75 |  |  | 255.72
1996-06-23 | 3232.89 |  |  | 255.88
1996-06-22 | 3232.99 |  |  | 256.08
1996-06-21 | 3233.19 |  |  | 255.81
1996-06-20 | 3233.35 |  |  | 255.58
1996-06-19 | 3233.48 |  |  | 255.54
1996-06-18 | 3233.65 |  |  | 255.56
1996-06-17 | 3233.83 |  |  | 255.56
1996-06-16 | 3234.01 |  |  | 255.54
1996-06-15 | 3234.18 |  |  | 255.56
1996-06-14 | 3234.36 |  |  | 255.54
1996-06-13 | 3234.52 |  |  | 279.34
1996-06-12 | 3234.71 |  |  | 314.2
1996-06-11 | 3234.91 |  |  | 314.25
1996-06-10 | 3235.09 |  |  | 318.84
1996-06-09 | 3235.25 |  |  | 327.35
1996-06-08 | 3235.52 |  |  | 338.51
1996-06-07 | 3235.72 |  |  | 350.75
1996-06-06 | 3235.86 |  |  | 338.27
1996-06-05 | 3236.03 |  |  | 319.15
1996-06-04 | 3236.15 |  |  | 331.37
1996-06-03 | 3236.24 |  |  | 369.48
1996-06-02 | 3236.38 |  |  | 416.06
1996-06-01 | 3236.48 |  |  | 430.4
1996-05-31 | 3236.59 |  |  | 466.82
1996-05-30 | 3236.7 |  |  | 543.39
1996-05-29 | 3236.88 |  |  | 602.41
1996-05-28 | 3237.05 |  |  | 625.49
1996-05-27 | 3237.21 |  |  | 644.22
1996-05-26 | 3237.26 |  |  | 656.46
1996-05-25 | 3237.26 |  |  | 655.47
1996-05-24 | 3237.18 |  |  | 640.84
1996-05-23 | 3237 |  |  | 611.89
1996-05-22 | 3236.78 |  |  | 581.94
1996-05-21 | 3236.63 |  |  | 568.87
1996-05-20 | 3236.53 |  |  | 465.88
1996-05-19 | 3236.24 |  |  | 323.22
1996-05-18 | 3235.76 |  |  | 279.26
1996-05-17 | 3235.36 |  |  | 258.59
1996-05-16 | 3235.33 |  |  | 249.22
1996-05-15 | 3235.23 |  |  | 245.69
1996-05-14 | 3235.23 |  |  | 223.03
1996-05-13 | 3235.22 |  |  | 215.02
1996-05-12 | 3235.26 |  |  | 244.84
1996-05-11 | 3235.26 |  |  | 244.91
1996-05-10 | 3235.26 |  |  | 245.42
1996-05-09 | 3235.22 |  |  | 245.79
1996-05-08 | 3235.21 |  |  | 245.44
1996-05-07 | 3235.21 |  |  | 243.73
1996-05-06 | 3235.17 |  |  | 241.36
1996-05-05 | 3235.12 |  |  | 239.57
1996-05-04 | 3235.04 |  |  | 237.66
1996-05-03 | 3234.93 |  |  | 267.13
1996-05-02 | 3234.89 |  |  | 357.27
1996-05-01 | 3234.87 |  |  | 468.08
1996-04-30 | 3234.84 |  |  | 631.08
1996-04-29 | 3234.86 |  |  | 935.32
1996-04-28 | 3235.07 |  |  | 1095.68
1996-04-27 | 3235.16 |  |  | 1101.27
1996-04-26 | 3235.16 |  |  | 1100.66
1996-04-25 | 3235.05 |  |  | 1094.48
1996-04-24 | 3234.51 |  |  | 534.82
1996-04-23 | 3233.7 |  |  | 208.54
1996-04-22 | 3233.16 |  |  | 207.23
1996-04-21 | 3232.97 |  |  | 207.23
1996-04-20 | 3232.83 |  |  | 207.21
1996-04-19 | 3232.71 |  |  | 207.21
1996-04-18 | 3232.6 |  |  | 207
1996-04-17 | 3232.44 |  |  | 206.43
1996-04-16 | 3232.25 |  |  | 206.06
1996-04-15 | 3232.1 |  |  | 205.78
1996-04-14 | 3231.95 |  |  | 205.31
1996-04-13 | 3231.71 |  |  | 205.31
1996-04-12 | 3231.42 |  |  | 205.09
1996-04-11 | 3231.09 |  |  | 204.23
1996-04-10 | 3230.78 |  |  | 203.47
1996-04-09 | 3230.41 |  |  | 203.47
1996-04-08 | 3230.09 |  |  | 203.09
1996-04-07 | 3229.73 |  |  | 201.63
1996-04-06 | 3229.44 |  |  | 201.63
1996-04-05 | 3229.16 |  |  | 201.63
1996-04-04 | 3228.85 |  |  | 201.62
1996-04-03 | 3228.52 |  |  | 201.07
1996-04-02 | 3228.14 |  |  | 200.11
1996-04-01 | 3227.68 |  |  | 199.82
1996-03-31 | 3227.35 |  |  | 214.35
1996-03-30 | 3227.14 |  |  | 224.26
1996-03-29 | 3226.96 |  |  | 224.26
1996-03-28 | 3226.73 |  |  | 223.81
1996-03-27 | 3226.51 |  |  | 222.77
1996-03-26 | 3226.26 |  |  | 222.35
1996-03-25 | 3226 |  |  | 222.32
1996-03-24 | 3225.74 |  |  | 222.32
1996-03-23 | 3225.42 |  |  | 222.32
1996-03-22 | 3225.03 |  |  | 221.69
1996-03-21 | 3224.61 |  |  | 298.05
1996-03-20 | 3224.17 |  |  | 423.45
1996-03-19 | 3223.86 |  |  | 530.3
1996-03-18 | 3223.64 |  |  | 613.23
1996-03-17 | 3223.43 |  |  | 636.93
1996-03-16 | 3223.13 |  |  | 687.64
1996-03-15 | 3222.83 |  |  | 797.85
1996-03-14 | 3222.51 |  |  | 892.98
1996-03-13 | 3222.12 |  |  | 906.98
1996-03-12 | 3221.49 |  |  | 906.14
1996-03-11 | 3220.81 |  |  | 902.99
1996-03-10 | 3220.46 |  |  | 901.25
1996-03-09 | 3220.05 |  |  | 901.02
1996-03-08 | 3219.71 |  |  | 900.62
1996-03-07 | 3219.77 |  |  | 901.02
1996-03-06 | 3219.87 |  |  | 900.85
1996-03-05 | 3219.88 |  |  | 912.6
1996-03-04 | 3219.9 |  |  | 923.36
1996-03-03 | 3219.98 |  |  | 923.3
1996-03-02 | 3220.21 |  |  | 923.48
1996-03-01 | 3220.56 |  |  | 979.53
1996-02-29 | 3220.89 |  |  | 1197.22
1996-02-28 | 3221.37 |  |  | 1457.73
1996-02-27 | 3221.97 |  |  | 1722.8
1996-02-26 | 3222.84 |  |  | 2058.13
1996-02-25 | 3223.82 |  |  | 2213.63
1996-02-24 | 3224.82 |  |  | 2221.44
1996-02-23 | 3225.76 |  |  | 2229.15
1996-02-22 | 3226.53 |  |  | 2233.66
1996-02-21 | 3227.16 |  |  | 2093.65
1996-02-20 | 3227.16 |  |  | 1992.26
1996-02-19 | 3227 |  |  | 1867.54
1996-02-18 | 3226.42 |  |  | 1752.14
1996-02-17 | 3226.05 |  |  | 1751.06
1996-02-16 | 3226.26 |  |  | 1775.44
1996-02-15 | 3226.68 |  |  | 1909.25
1996-02-14 | 3227.16 |  |  | 2135.83
1996-02-13 | 3227.7 |  |  | 2399.5
1996-02-12 | 3228.4 |  |  | 2774.46
1996-02-11 | 3229.12 |  |  | 2978.56
1996-02-10 | 3229.35 |  |  | 2986.05
1996-02-09 | 3228.34 |  |  | 2158.93
1996-02-08 | 3224.42 |  |  | 1344.8
1996-02-07 | 3220.82 |  |  | 621.63
1996-02-06 | 3219.12 |  |  | 262.08
1996-02-05 | 3219.12 |  |  | 262.14
1996-02-04 | 3219.13 |  |  | 262.08
1996-02-03 | 3219.24 |  |  | 262.1
1996-02-02 | 3219.36 |  |  | 262.08
1996-02-01 | 3219.41 |  |  | 262.08
1996-01-31 | 3219.44 |  |  | 262.08
1996-01-30 | 3219.5 |  |  | 262.08
1996-01-29 | 3219.51 |  |  | 262.08
1996-01-28 | 3219.51 |  |  | 262.08
1996-01-27 | 3219.51 |  |  | 262.12
1996-01-26 | 3219.47 |  |  | 262.08
1996-01-25 | 3219.46 |  |  | 262.08
1996-01-24 | 3219.45 |  |  | 262.1
1996-01-23 | 3219.44 |  |  | 220.63
1996-01-22 | 3219.34 |  |  | 158.89
1996-01-21 | 3219.19 |  |  | 158.89
1996-01-20 | 3219.05 |  |  | 158.89
1996-01-19 | 3218.87 |  |  | 158.89
1996-01-18 | 3218.7 |  |  | 158.85
1996-01-17 | 3218.43 |  |  | 158.21
1996-01-16 | 3217.98 |  |  | 157.32
1996-01-15 | 3217.49 |  |  | 157.19
1996-01-14 | 3217.21 |  |  | 157.1
1996-01-13 | 3216.92 |  |  | 157.1
1996-01-12 | 3216.57 |  |  | 145.21
1996-01-11 | 3214.07 |  |  | 130.69
1996-01-10 | 3214.07 |  |  | 130.08
1996-01-09 | 3213.84 |  |  | 130.08
1996-01-08 | 3213 |  |  | 130.08
1996-01-07 | 3212.68 |  |  | 130.08
1996-01-06 | 3212.48 |  |  | 130.08
1996-01-05 | 3212.22 |  |  | 139.6
1996-01-04 | 3211.93 |  |  | 153.58
1996-01-03 | 3211.59 |  |  | 153.63
1996-01-02 | 3211.32 |  |  | 153.57
1996-01-01 | 3210.88 |  |  | 153.57
1995-12-31 | 3210.32 |  |  | 153.57
1995-12-30 | 3210.1 |  |  | 153.57
1995-12-29 | 3210.1 |  |  | 153.57
1995-12-28 | 3210.1 |  |  | 153.57
1995-12-27 | 3210.12 |  |  | 153.57
1995-12-26 | 3210.19 |  |  | 225
1995-12-25 | 3210.28 |  |  | 300
1995-12-24 | 3210.32 |  |  | 375
1995-12-23 | 3210.33 |  |  | 450
1995-12-22 | 3210.33 |  |  | 525
1995-12-21 | 3210.48 |  |  | 597.26
1995-12-20 | 3210.76 |  |  | 705.96
1995-12-19 | 3211.2 |  |  | 887.85
1995-12-18 | 3211.81 |  |  | 1021.22
1995-12-17 | 3212.42 |  |  | 1046.96
1995-12-16 | 3212.95 |  |  | 1050.05
1995-12-15 | 3213.42 |  |  | 1053.56
1995-12-14 | 3213.66 |  |  | 1056.76
1995-12-13 | 3213.66 |  |  | 1057.69
1995-12-12 | 3213.15 |  |  | 642.48
1995-12-11 | 3212.29 |  |  | 184.02
1995-12-10 | 3212 |  |  | 116.11
1995-12-09 | 3211.94 |  |  | 116.11
1995-12-08 | 3211.92 |  |  | 116.09
1995-12-07 | 3211.8 |  |  | 115.85
1995-12-06 | 3211.75 |  |  | 115.77
1995-12-05 | 3211.73 |  |  | 116.13
1995-12-04 | 3211.65 |  |  | 116.14
1995-12-03 | 3211.63 |  |  | 116.14
1995-12-02 | 3211.56 |  |  | 116.13
1995-12-01 | 3211.48 |  |  | 116.14
1995-11-30 | 3211.46 |  |  | 116.08
1995-11-29 | 3211.48 |  |  | 115.95
1995-11-28 | 3211.48 |  |  | 116.13
1995-11-27 | 3211.52 |  |  | 116.09
1995-11-26 | 3211.54 |  |  | 116.14
1995-11-25 | 3211.57 |  |  | 116.14
1995-11-24 | 3211.58 |  |  | 116.14
1995-11-23 | 3211.62 |  |  | 116.13
1995-11-22 | 3211.67 |  |  | 116.14
1995-11-21 | 3211.73 |  |  | 116.14
1995-11-20 | 3211.74 |  |  | 116.14
1995-11-19 | 3211.8 |  |  | 116.14
1995-11-18 | 3211.86 |  |  | 116.14
1995-11-17 | 3211.86 |  |  | 116.14
1995-11-16 | 3211.94 |  |  | 116.14
1995-11-15 | 3211.99 |  |  | 116.14
1995-11-14 | 3212.03 |  |  | 116.14
1995-11-13 | 3212.06 |  |  | 116.14
1995-11-12 | 3212.08 |  |  | 116.14
1995-11-11 | 3212.08 |  |  | 116.14
1995-11-10 | 3212.08 |  |  | 116.14
1995-11-09 | 3212.16 |  |  | 116.14
1995-11-08 | 3212.21 |  |  | 115.42
1995-11-07 | 3212.25 |  |  | 114.65
1995-11-06 | 3212.3 |  |  | 114.65
1995-11-05 | 3212.35 |  |  | 114.65
1995-11-04 | 3212.39 |  |  | 114.65
1995-11-03 | 3212.46 |  |  | 114.65
1995-11-02 | 3212.53 |  |  | 114.65
1995-11-01 | 3212.6 |  |  | 114.65
1995-10-31 | 3212.65 |  |  | 104.32
1995-10-30 | 3212.69 |  |  | 88.31
1995-10-29 | 3212.73 |  |  | 88.31
1995-10-28 | 3212.77 |  |  | 88.31
1995-10-27 | 3212.79 |  |  | 81.11
1995-10-26 | 3212.81 |  |  | 70.21
1995-10-25 | 3212.82 |  |  | 70.21
1995-10-24 | 3212.78 |  |  | 70.21
1995-10-23 | 3212.78 |  |  | 87.57
1995-10-22 | 3212.88 |  |  | 113.16
1995-10-21 | 3212.95 |  |  | 113.16
1995-10-20 | 3213.04 |  |  | 113.16
1995-10-19 | 3213.12 |  |  | 113.16
1995-10-18 | 3213.18 |  |  | 113.16
1995-10-17 | 3213.26 |  |  | 113.16
1995-10-16 | 3213.36 |  |  | 113.16
1995-10-15 | 3213.44 |  |  | 113.16
1995-10-14 | 3213.52 |  |  | 113.74
1995-10-13 | 3213.61 |  |  | 114.55
1995-10-12 | 3213.67 |  |  | 130.56
1995-10-11 | 3213.8 |  |  | 141.64
1995-10-10 | 3213.95 |  |  | 141.69
1995-10-09 | 3214.05 |  |  | 141.55
1995-10-08 | 3214.14 |  |  | 141.55
1995-10-07 | 3214.31 |  |  | 141.55
1995-10-06 | 3214.41 |  |  | 141.55
1995-10-05 | 3214.55 |  |  | 141.59
1995-10-04 | 3214.68 |  |  | 141.55
1995-10-03 | 3214.77 |  |  | 141.66
1995-10-02 | 3214.92 |  |  | 141.55
1995-10-01 | 3215.02 |  |  | 141.55
1995-09-30 | 3215.1 |  |  | 141.55
1995-09-29 | 3215.22 |  |  | 141.55
1995-09-28 | 3215.34 |  |  | 141.67
1995-09-27 | 3215.46 |  |  | 141.62
1995-09-26 | 3215.58 |  |  | 141.59
1995-09-25 | 3215.7 |  |  | 141.8
1995-09-24 | 3215.87 |  |  | 141.55
1995-09-23 | 3216 |  |  | 141.59
1995-09-22 | 3216.09 |  |  | 141.55
1995-09-21 | 3216.29 |  |  | 141.55
1995-09-20 | 3216.48 |  |  | 141.57
1995-09-19 | 3216.58 |  |  | 142.54
1995-09-18 | 3216.69 |  |  | 143.23
1995-09-17 | 3216.86 |  |  | 143.23
1995-09-16 | 3216.97 |  |  | 143.23
1995-09-15 | 3217.13 |  |  | 143.23
1995-09-14 | 3217.27 |  |  | 143.23
1995-09-13 | 3217.41 |  |  | 143.23
1995-09-12 | 3217.54 |  |  | 143.23
1995-09-11 | 3217.66 |  |  | 143.23
1995-09-10 | 3217.8 |  |  | 143.23
1995-09-09 | 3217.93 |  |  | 143.23
1995-09-08 | 3218.01 |  |  | 155.38
1995-09-07 | 3218.2 |  |  | 167.98
1995-09-06 | 3218.34 |  |  | 168
1995-09-05 | 3218.48 |  |  | 167.98
1995-09-04 | 3218.63 |  |  | 167.98
1995-09-03 | 3218.8 |  |  | 167.98
1995-09-02 | 3218.96 |  |  | 167.98
1995-09-01 | 3219.1 |  |  | 167.98
1995-08-31 | 3219.23 |  |  | 188.97
1995-08-30 | 3219.41 |  |  | 213.03
1995-08-29 | 3219.59 |  |  | 214.43
1995-08-28 | 3219.81 |  |  | 214.6
1995-08-27 | 3220.01 |  |  | 214.57
1995-08-26 | 3220.21 |  |  | 214.68
1995-08-25 | 3220.45 |  |  | 214.68
1995-08-24 | 3220.66 |  |  | 214.68
1995-08-23 | 3220.86 |  |  | 214.68
1995-08-22 | 3221.08 |  |  | 214.68
1995-08-21 | 3221.26 |  |  | 214.68
1995-08-20 | 3221.44 |  |  | 214.68
1995-08-19 | 3221.59 |  |  | 214.68
1995-08-18 | 3221.73 |  |  | 214.68
1995-08-17 | 3221.94 |  |  | 214.68
1995-08-16 | 3222.12 |  |  | 214.68
1995-08-15 | 3222.34 |  |  | 214.68
1995-08-14 | 3222.56 |  |  | 214.68
1995-08-13 | 3222.73 |  |  | 214.68
1995-08-12 | 3222.89 |  |  | 214.72
1995-08-11 | 3223.12 |  |  | 214.68
1995-08-10 | 3223.33 |  |  | 214.8
1995-08-09 | 3223.56 |  |  | 214.7
1995-08-08 | 3223.74 |  |  | 213.75
1995-08-07 | 3223.9 |  |  | 214.54
1995-08-06 | 3224.16 |  |  | 214.54
1995-08-05 | 3224.32 |  |  | 214.58
1995-08-04 | 3224.46 |  |  | 214.62
1995-08-03 | 3224.64 |  |  | 214.65
1995-08-02 | 3224.81 |  |  | 214.68
1995-08-01 | 3225 |  |  | 214.64
1995-07-31 | 3225.17 |  |  | 214.68
1995-07-30 | 3225.34 |  |  | 214.68
1995-07-29 | 3225.52 |  |  | 214.74
1995-07-28 | 3225.78 |  |  | 214.7
1995-07-27 | 3225.96 |  |  | 214.74
1995-07-26 | 3226.1 |  |  | 214.86
1995-07-25 | 3226.35 |  |  | 214.68
1995-07-24 | 3226.51 |  |  | 214.76
1995-07-23 | 3226.67 |  |  | 215.32
1995-07-22 | 3226.85 |  |  | 215.71
1995-07-21 | 3227.02 |  |  | 216.02
1995-07-20 | 3227.2 |  |  | 216.53
1995-07-19 | 3227.31 |  |  | 216.54
1995-07-18 | 3227.46 |  |  | 216.56
1995-07-17 | 3227.58 |  |  | 216.58
1995-07-16 | 3227.72 |  |  | 216.58
1995-07-15 | 3227.83 |  |  | 216.58
1995-07-14 | 3228 |  |  | 216.58
1995-07-13 | 3228.14 |  |  | 216.58
1995-07-12 | 3228.28 |  |  | 216.62
1995-07-11 | 3228.47 |  |  | 216.94
1995-07-10 | 3228.61 |  |  | 217.24
1995-07-09 | 3228.79 |  |  | 218.35
1995-07-08 | 3228.94 |  |  | 218.4
1995-07-07 | 3229.13 |  |  | 231.48
1995-07-06 | 3229.25 |  |  | 234.43
1995-07-05 | 3229.44 |  |  | 234.39
1995-07-04 | 3229.64 |  |  | 234.44
1995-07-03 | 3229.82 |  |  | 234.9
1995-07-02 | 3229.97 |  |  | 235.28
1995-07-01 | 3230.14 |  |  | 235.1
1995-06-30 | 3230.27 |  |  | 235.13
1995-06-29 | 3230.38 |  |  | 235.61
1995-06-28 | 3230.53 |  |  | 236.09
1995-06-27 | 3230.71 |  |  | 236.16
1995-06-26 | 3230.85 |  |  | 236.37
1995-06-25 | 3230.99 |  |  | 236.35
1995-06-24 | 3231.17 |  |  | 235.88
1995-06-23 | 3231.25 |  |  | 235.52
1995-06-22 | 3231.38 |  |  | 235.52
1995-06-21 | 3231.46 |  |  | 235.24
1995-06-20 | 3231.54 |  |  | 247.32
1995-06-19 | 3231.66 |  |  | 260.16
1995-06-18 | 3231.77 |  |  | 260.3
1995-06-17 | 3231.88 |  |  | 260.32
1995-06-16 | 3231.96 |  |  | 312.78
1995-06-15 | 3232.11 |  |  | 364.07
1995-06-14 | 3232.31 |  |  | 365.01
1995-06-13 | 3232.49 |  |  | 365.2
1995-06-12 | 3232.74 |  |  | 309.3
1995-06-11 | 3232.89 |  |  | 228.23
1995-06-10 | 3232.99 |  |  | 228.23
1995-06-09 | 3233.01 |  |  | 228.23
1995-06-08 | 3233.07 |  |  | 228
1995-06-07 | 3233.11 |  |  | 227.89
1995-06-06 | 3233.16 |  |  | 227.75
1995-06-05 | 3233.23 |  |  | 227.83
1995-06-04 | 3233.32 |  |  | 227.33
1995-06-03 | 3233.38 |  |  | 226.54
1995-06-02 | 3233.42 |  |  | 226.33
1995-06-01 | 3233.53 |  |  | 226.29
1995-05-31 | 3233.65 |  |  | 226.2
1995-05-30 | 3233.76 |  |  | 226.2
1995-05-29 | 3233.87 |  |  | 226.2
1995-05-28 | 3233.97 |  |  | 225.56
1995-05-27 | 3234.05 |  |  | 225.23
1995-05-26 | 3234.15 |  |  | 237.14
1995-05-25 | 3234.24 |  |  | 253.41
1995-05-24 | 3234.29 |  |  | 250
1995-05-23 | 3234.45 |  |  | 408.23
1995-05-22 | 3234.62 |  |  | 483.41
1995-05-21 | 3234.87 |  |  | 531.06
1995-05-20 | 3235.1 |  |  | 533.69
1995-05-19 | 3235.31 |  |  | 543.53
1995-05-18 | 3235.55 |  |  | 556.25
1995-05-17 | 3235.71 |  |  | 570.59
1995-05-16 | 3235.91 |  |  | 584.68
1995-05-15 | 3236.06 |  |  | 598.23
1995-05-14 | 3236.16 |  |  | 608.47
1995-05-13 | 3236.17 |  |  | 616.79
1995-05-12 | 3236.17 |  |  | 620.03
1995-05-11 | 3236.21 |  |  | 621.93
1995-05-10 | 3236.21 |  |  | 624.36
1995-05-09 | 3236.21 |  |  | 627.96
1995-05-08 | 3236.21 |  |  | 627.84
1995-05-07 | 3236.21 |  |  | 622.84
1995-05-06 | 3236.15 |  |  | 616.11
1995-05-05 | 3236.14 |  |  | 609.89
1995-05-04 | 3236.15 |  |  | 610.82
1995-05-03 | 3236.15 |  |  | 611.98
1995-05-02 | 3236.15 |  |  | 606.79
1995-05-01 | 3236.15 |  |  | 572.86
1995-04-30 | 3236.25 |  |  | 491.29
1995-04-29 | 3236.29 |  |  | 475.69
1995-04-28 | 3236.33 |  |  | 466.38
1995-04-27 | 3236.45 |  |  | 416
1995-04-26 | 3236.55 |  |  | 373.45
1995-04-25 | 3236.64 |  |  | 381.79
1995-04-24 | 3236.71 |  |  | 392.07
1995-04-23 | 3236.77 |  |  | 408.29
1995-04-22 | 3236.84 |  |  | 416.81
1995-04-21 | 3236.85 |  |  | 442.35
1995-04-20 | 3236.93 |  |  | 514.76
1995-04-19 | 3237.05 |  |  | 583.04
1995-04-18 | 3237.21 |  |  | 627.15
1995-04-17 | 3237.37 |  |  | 646.43
1995-04-16 | 3237.49 |  |  | 664.35
1995-04-15 | 3237.55 |  |  | 679.18
1995-04-14 | 3237.55 |  |  | 553.81
1995-04-13 | 3237.44 |  |  | 371.16
1995-04-12 | 3237.33 |  |  | 353.78
1995-04-11 | 3237.17 |  |  | 335.85
1995-04-10 | 3236.87 |  |  | 307.36
1995-04-09 | 3236.65 |  |  | 275.42
1995-04-08 | 3236.27 |  |  | 231.54
1995-04-07 | 3236.06 |  |  | 213.55
1995-04-06 | 3235.85 |  |  | 197.41
1995-04-05 | 3235.69 |  |  | 182.69
1995-04-04 | 3235.55 |  |  | 167.62
1995-04-03 | 3235.46 |  |  | 154.07
1995-04-02 | 3235.39 |  |  | 149.26
1995-04-01 | 3235.24 |  |  | 147.62
1995-03-31 | 3235.1 |  |  | 142.44
1995-03-30 | 3234.94 |  |  | 141.55
1995-03-29 | 3234.75 |  |  | 141.55
1995-03-28 | 3234.5 |  |  | 141.55
1995-03-27 | 3234.32 |  |  | 141.49
1995-03-26 | 3234.06 |  |  | 140.41
1995-03-25 | 3233.75 |  |  | 140.05
1995-03-24 | 3233.39 |  |  | 140.18
1995-03-23 | 3232.97 |  |  | 139.91
1995-03-22 | 3232.51 |  |  | 139.91
1995-03-21 | 3231.92 |  |  | 139.88
1995-03-20 | 3231.25 |  |  | 139.49
1995-03-19 | 3230.36 |  |  | 138.51
1995-03-18 | 3229.09 |  |  | 138.24
1995-03-17 | 3228.39 |  |  | 138.22
1995-03-16 | 3227.48 |  |  | 136.71
1995-03-15 | 3226.68 |  |  | 136.57
1995-03-14 | 3225.64 |  |  | 136.62
1995-03-13 | 3224.82 |  |  | 136.57
1995-03-12 | 3224.46 |  |  | 136.35
1995-03-11 | 3223.96 |  |  | 135.55
1995-03-10 | 3223.45 |  |  | 135.24
1995-03-09 | 3223.06 |  |  | 159.3
1995-03-08 | 3222.82 |  |  | 240.17
1995-03-07 | 3222.77 |  |  | 343.63
1995-03-06 | 3222.83 |  |  | 455.37
1995-03-05 | 3222.93 |  |  | 499.4
1995-03-04 | 3222.96 |  |  | 499.4
1995-03-03 | 3222.97 |  |  | 499.4
1995-03-02 | 3222.97 |  |  | 499.4
1995-03-01 | 3222.97 |  |  | 499.4
1995-02-28 | 3222.94 |  |  | 499.4
1995-02-27 | 3222.83 |  |  | 499.4
1995-02-26 | 3222.68 |  |  | 499.29
1995-02-25 | 3222.43 |  |  | 498.42
1995-02-24 | 3222.14 |  |  | 496.45
1995-02-23 | 3221.79 |  |  | 495.87
1995-02-22 | 3221.39 |  |  | 495.87
1995-02-21 | 3220.91 |  |  | 495.04
1995-02-20 | 3220.32 |  |  | 492.49
1995-02-19 | 3219.55 |  |  | 492.06
1995-02-18 | 3218.69 |  |  | 490.54
1995-02-17 | 3218.62 |  |  | 491.29
1995-02-16 | 3218.77 |  |  | 491.38
1995-02-15 | 3218.86 |  |  | 492.32
1995-02-14 | 3218.94 |  |  | 492.32
1995-02-13 | 3219.03 |  |  | 491.99
1995-02-12 | 3219.02 |  |  | 491.84
1995-02-11 | 3219.02 |  |  | 492.32
1995-02-10 | 3218.98 |  |  | 492.36
1995-02-09 | 3218.93 |  |  | 492.36
1995-02-08 | 3218.82 |  |  | 492
1995-02-07 | 3218.48 |  |  | 51.21
1995-02-06 | 3217.82 |  |  | 51.07
1995-02-05 | 3214.29 |  |  | 51.07
1995-02-04 | 3214.29 |  |  | 51.07
1995-02-03 | 3214.29 |  |  | 50.69
1995-02-02 | 3212 |  |  | 50.21
1995-02-01 | 3208.47 |  |  | 49.34
1995-01-31 | 3203.33 |  |  | 48.33
1995-01-30 | 3197.97 |  |  | 47.71
1995-01-29 | 3195.96 |  |  | 47.66
1995-01-28 | 3195.33 |  |  | 47.7
1995-01-27 | 3195.08 |  |  | 47.67
1995-01-26 | 3194.93 |  |  | 47.67
1995-01-25 | 3194.83 |  |  | 47.67
1995-01-24 | 3194.72 |  |  | 47.67
1995-01-23 | 3194.58 |  |  | 47.67
1995-01-22 | 3194.5 |  |  | 47.67
1995-01-21 | 3194.4 |  |  | 47.67
1995-01-20 | 3194.29 |  |  | 47.67
1995-01-19 | 3194.13 |  |  | 47.67
1995-01-18 | 3193.94 |  |  | 47.67
1995-01-17 | 3193.77 |  |  | 47.67
1995-01-16 | 3193.48 |  |  | 47.67
1995-01-15 | 3192.96 |  |  | 47.67
1995-01-14 | 3192.04 |  |  | 47.71
1995-01-13 | 3191.66 |  |  | 47.69
1995-01-12 | 3191.38 |  |  | 47.4
1995-01-11 | 3191.05 |  |  | 47.37
1995-01-10 | 3190.52 |  |  | 47.14
1995-01-09 | 3190.42 |  |  | 47.26
1995-01-08 | 3190.35 |  |  | 47.14
1995-01-07 | 3190.31 |  |  | 47.23
1995-01-06 | 3190.28 |  |  | 46.86
1995-01-05 | 3190.24 |  |  | 46.9
1995-01-04 | 3190.24 |  |  | 46.95
1995-01-03 | 3190.24 |  |  | 47.3
1995-01-02 | 3190.24 |  |  | 47.32
1995-01-01 | 3190.24 |  |  | 47.52
1994-12-31 | 3190.24 |  |  | 47.63
1994-12-30 | 3190.22 |  |  | 47.67
1994-12-29 | 3190.22 |  |  | 47.67
1994-12-28 | 3190.22 |  |  | 47.67
1994-12-27 | 3190.2 |  |  | 47.67
1994-12-26 | 3190.14 |  |  | 47.69
1994-12-25 | 3190.11 |  |  | 47.67
1994-12-24 | 3190.07 |  |  | 47.67
1994-12-23 | 3190.02 |  |  | 47.67
1994-12-22 | 3189.99 |  |  | 47.67
1994-12-21 | 3189.94 |  |  | 47.67
1994-12-20 | 3189.87 |  |  | 47.67
1994-12-19 | 3189.83 |  |  | 47.68
1994-12-18 | 3189.76 |  |  | 47.67
1994-12-17 | 3189.72 |  |  | 47.67
1994-12-16 | 3189.68 |  |  | 47.64
1994-12-15 | 3189.64 |  |  | 47.63
1994-12-14 | 3189.6 |  |  | 47.25
1994-12-13 | 3189.59 |  |  | 47
1994-12-12 | 3189.57 |  |  | 46.89
1994-12-11 | 3189.56 |  |  | 47.01
1994-12-10 | 3189.54 |  |  | 46.92
1994-12-09 | 3189.52 |  |  | 46.85
1994-12-08 | 3189.48 |  |  | 46.84
1994-12-07 | 3189.46 |  |  | 46.87
1994-12-06 | 3189.46 |  |  | 46.9
1994-12-05 | 3189.46 |  |  | 46.84
1994-12-04 | 3189.46 |  |  | 47
1994-12-03 | 3189.46 |  |  | 47.41
1994-12-02 | 3189.44 |  |  | 47.28
1994-12-01 | 3189.41 |  |  | 47.19
1994-11-30 | 3189.36 |  |  | 46.84
1994-11-29 | 3189.29 |  |  | 46.84
1994-11-28 | 3189.25 |  |  | 46.84
1994-11-27 | 3189.25 |  |  | 46.84
1994-11-26 | 3189.21 |  |  | 46.84
1994-11-25 | 3189.21 |  |  | 46.84
1994-11-24 | 3189.2 |  |  | 46.85
1994-11-23 | 3189.2 |  |  | 46.84
1994-11-22 | 3189.2 |  |  | 46.85
1994-11-21 | 3189.2 |  |  | 46.84
1994-11-20 | 3189.2 |  |  | 46.84
1994-11-19 | 3189.2 |  |  | 46.84
1994-11-18 | 3189.19 |  |  | 46.84
1994-11-17 | 3189.17 |  |  | 46.84
1994-11-16 | 3189.16 |  |  | 46.84
1994-11-15 | 3189.16 |  |  | 46.87
1994-11-14 | 3189.15 |  |  | 46.84
1994-11-13 | 3189.12 |  |  | 46.84
1994-11-12 | 3189.12 |  |  | 46.84
1994-11-11 | 3189.11 |  |  | 46.84
1994-11-10 | 3189.06 |  |  | 46.84
1994-11-09 | 3189.06 |  |  | 46.87
1994-11-08 | 3189.06 |  |  | 46.87
1994-11-07 | 3188.99 |  |  | 46.84
1994-11-06 | 3188.97 |  |  | 46.84
1994-11-05 | 3188.95 |  |  | 46.84
1994-11-04 | 3188.95 |  |  | 46.84
1994-11-03 | 3188.89 |  |  | 46.84
1994-11-02 | 3188.89 |  |  | 46.84
1994-11-01 | 3188.89 |  |  | 46.97
1994-10-31 | 3188.85 |  |  | 46.93
1994-10-30 | 3188.86 |  |  | 46.84
1994-10-29 | 3188.86 |  |  | 46.84
1994-10-28 | 3188.86 |  |  | 46.84
1994-10-27 | 3188.86 |  |  | 47.05
1994-10-26 | 3188.85 |  |  | 46.84
1994-10-25 | 3188.87 |  |  | 46.84
1994-10-24 | 3188.89 |  |  | 47.21
1994-10-23 | 3188.86 |  |  | 47.67
1994-10-22 | 3188.88 |  |  | 47.67
1994-10-21 | 3188.89 |  |  | 47.67
1994-10-20 | 3188.9 |  |  | 46.21
1994-10-19 | 3188.92 |  |  | 41.89
1994-10-18 | 3188.92 |  |  | 61.68
1994-10-17 | 3189 |  |  | 116.81
1994-10-16 | 3189.13 |  |  | 143.23
1994-10-15 | 3189.27 |  |  | 143.23
1994-10-14 | 3189.41 |  |  | 144.17
1994-10-13 | 3189.58 |  |  | 158.54
1994-10-12 | 3189.78 |  |  | 167.98
1994-10-11 | 3190 |  |  | 167.98
1994-10-10 | 3190.26 |  |  | 168.06
1994-10-09 | 3190.45 |  |  | 168.14
1994-10-08 | 3190.72 |  |  | 168.18
1994-10-07 | 3190.93 |  |  | 168.23
1994-10-06 | 3191.18 |  |  | 168.53
1994-10-05 | 3191.39 |  |  | 168.97
1994-10-04 | 3191.63 |  |  | 169.49
1994-10-03 | 3191.85 |  |  | 190.65
1994-10-02 | 3192.17 |  |  | 210.93
1994-10-01 | 3192.46 |  |  | 210.93
1994-09-30 | 3192.75 |  |  | 211.15
1994-09-29 | 3192.95 |  |  | 212.71
1994-09-28 | 3193.24 |  |  | 212.79
1994-09-27 | 3193.54 |  |  | 212.79
1994-09-26 | 3193.83 |  |  | 201.51
1994-09-25 | 3194.1 |  |  | 192.57
1994-09-24 | 3194.34 |  |  | 192.57
1994-09-23 | 3194.59 |  |  | 192.57
1994-09-22 | 3194.84 |  |  | 192.57
1994-09-21 | 3195.07 |  |  | 197.85
1994-09-20 | 3195.32 |  |  | 203.47
1994-09-19 | 3195.62 |  |  | 203.47
1994-09-18 | 3195.84 |  |  | 203.47
1994-09-17 | 3196.09 |  |  | 203.47
1994-09-16 | 3196.31 |  |  | 220.48
1994-09-15 | 3196.6 |  |  | 239.25
1994-09-14 | 3197.05 |  |  | 240.13
1994-09-13 | 3197.05 |  |  | 259.96
1994-09-12 | 3197.47 |  |  | 275.62
1994-09-11 | 3197.75 |  |  | 276.88
1994-09-10 | 3198.13 |  |  | 277.84
1994-09-09 | 3198.45 |  |  | 277.95
1994-09-08 | 3198.84 |  |  | 277.95
1994-09-07 | 3199.23 |  |  | 278.1
1994-09-06 | 3199.59 |  |  | 285.18
1994-09-05 | 3199.93 |  |  | 294.34
1994-09-04 | 3200.3 |  |  | 294.56
1994-09-03 | 3200.66 |  |  | 294.74
1994-09-02 | 3201.05 |  |  | 295
1994-09-01 | 3201.41 |  |  | 296.74
1994-08-31 | 3201.78 |  |  | 296.98
1994-08-30 | 3202.15 |  |  | 296.98
1994-08-29 | 3202.54 |  |  | 297.48
1994-08-28 | 3202.87 |  |  | 299.22
1994-08-27 | 3203.25 |  |  | 299.41
1994-08-26 | 3203.61 |  |  | 299.46
1994-08-25 | 3204.01 |  |  | 300.7
1994-08-24 | 3204.32 |  |  | 301.79
1994-08-23 | 3204.69 |  |  | 301.85
1994-08-22 | 3204.85 |  |  | 301.85
1994-08-21 | 3205.22 |  |  | 302.53
1994-08-20 | 3205.59 |  |  | 304.18
1994-08-19 | 3205.93 |  |  | 304.29
1994-08-18 | 3206.31 |  |  | 304.32
1994-08-17 | 3206.69 |  |  | 306.35
1994-08-16 | 3207.01 |  |  | 249.45
1994-08-15 | 3207.33 |  |  | 212.79
1994-08-14 | 3207.59 |  |  | 212.79
1994-08-13 | 3207.82 |  |  | 212.79
1994-08-12 | 3208.06 |  |  | 212.79
1994-08-11 | 3208.34 |  |  | 212.81
1994-08-10 | 3208.58 |  |  | 212.95
1994-08-09 | 3208.81 |  |  | 213.17
1994-08-08 | 3209.03 |  |  | 214.61
1994-08-07 | 3209.28 |  |  | 214.68
1994-08-06 | 3209.54 |  |  | 214.68
1994-08-05 | 3209.76 |  |  | 214.68
1994-08-04 | 3210.03 |  |  | 214.68
1994-08-03 | 3210.28 |  |  | 214.72
1994-08-02 | 3210.46 |  |  | 215.04
1994-08-01 | 3210.74 |  |  | 216.29
1994-07-31 | 3210.96 |  |  | 216.58
1994-07-30 | 3211.23 |  |  | 216.58
1994-07-29 | 3211.46 |  |  | 216.58
1994-07-28 | 3211.72 |  |  | 216.58
1994-07-27 | 3211.93 |  |  | 216.58
1994-07-26 | 3212.17 |  |  | 216.58
1994-07-25 | 3212.41 |  |  | 216.58
1994-07-24 | 3212.65 |  |  | 216.72
1994-07-23 | 3212.87 |  |  | 216.91
1994-07-22 | 3213.09 |  |  | 217.42
1994-07-21 | 3213.23 |  |  | 217.71
1994-07-20 | 3213.47 |  |  | 218.25
1994-07-19 | 3213.68 |  |  | 218.48
1994-07-18 | 3213.89 |  |  | 218.48
1994-07-17 | 3214.13 |  |  | 218.48
1994-07-16 | 3214.35 |  |  | 218.48
1994-07-15 | 3214.57 |  |  | 218.48
1994-07-14 | 3214.74 |  |  | 218.54
1994-07-13 | 3214.94 |  |  | 218.59
1994-07-12 | 3215.15 |  |  | 218.87
1994-07-11 | 3215.4 |  |  | 219.2
1994-07-10 | 3215.62 |  |  | 220.09
1994-07-09 | 3215.83 |  |  | 220.28
1994-07-08 | 3216.06 |  |  | 220.4
1994-07-07 | 3216.31 |  |  | 220.4
1994-07-06 | 3216.42 |  |  | 220.4
1994-07-05 | 3216.64 |  |  | 220.52
1994-07-04 | 3216.88 |  |  | 220.64
1994-07-03 | 3217.11 |  |  | 220.89
1994-07-02 | 3217.32 |  |  | 222.09
1994-07-01 | 3217.56 |  |  | 222.3
1994-06-30 | 3217.8 |  |  | 222.28
1994-06-29 | 3217.96 |  |  | 222.32
1994-06-28 | 3218.16 |  |  | 209
1994-06-27 | 3218.33 |  |  | 201.63
1994-06-26 | 3218.49 |  |  | 201.63
1994-06-25 | 3218.68 |  |  | 197.76
1994-06-24 | 3218.89 |  |  | 190.78
1994-06-23 | 3219.09 |  |  | 191
1994-06-22 | 3219.29 |  |  | 190.99
1994-06-21 | 3219.44 |  |  | 190.83
1994-06-20 | 3219.61 |  |  | 190.83
1994-06-19 | 3219.76 |  |  | 190.85
1994-06-18 | 3219.89 |  |  | 190.85
1994-06-17 | 3220.05 |  |  | 235.7
1994-06-16 | 3220.2 |  |  | 253.36
1994-06-15 | 3220.4 |  |  | 253.38
1994-06-14 | 3220.67 |  |  | 253.42
1994-06-13 | 3220.86 |  |  | 233.94
1994-06-12 | 3221.07 |  |  | 203.47
1994-06-11 | 3221.21 |  |  | 203.47
1994-06-10 | 3221.33 |  |  | 201.77
1994-06-09 | 3221.43 |  |  | 194.34
1994-06-08 | 3221.55 |  |  | 194.36
1994-06-07 | 3221.61 |  |  | 194.38
1994-06-06 | 3221.73 |  |  | 194.4
1994-06-05 | 3221.84 |  |  | 194.38
1994-06-04 | 3222 |  |  | 194.36
1994-06-03 | 3222.11 |  |  | 190.15
1994-06-02 | 3222.23 |  |  | 185.73
1994-06-01 | 3222.35 |  |  | 186.65
1994-05-31 | 3222.46 |  |  | 187.03
1994-05-30 | 3222.58 |  |  | 186.87
1994-05-29 | 3222.69 |  |  | 187.05
1994-05-28 | 3222.8 |  |  | 187.03
1994-05-27 | 3222.93 |  |  | 187.03
1994-05-26 | 3223.1 |  |  | 187.03
1994-05-25 | 3223.25 |  |  | 187.03
1994-05-24 | 3223.38 |  |  | 187.03
1994-05-23 | 3223.44 |  |  | 187.03
1994-05-22 | 3223.5 |  |  | 187.03
1994-05-21 | 3223.51 |  |  | 187.03
1994-05-20 | 3223.56 |  |  | 187.05
1994-05-19 | 3223.64 |  |  | 187.16
1994-05-18 | 3223.7 |  |  | 187.03
1994-05-17 | 3223.79 |  |  | 187.05
1994-05-16 | 3223.89 |  |  | 187.09
1994-05-15 | 3223.99 |  |  | 187.36
1994-05-14 | 3224.11 |  |  | 187.05
1994-05-13 | 3224.21 |  |  | 187.05
1994-05-12 | 3224.34 |  |  | 178.02
1994-05-11 | 3224.45 |  |  | 177.36
1994-05-10 | 3224.55 |  |  | 177.36
1994-05-09 | 3224.63 |  |  | 177.3
1994-05-08 | 3224.66 |  |  | 177.29
1994-05-07 | 3224.67 |  |  | 177.12
1994-05-06 | 3224.67 |  |  | 177.09
1994-05-05 | 3224.65 |  |  | 178.32
1994-05-04 | 3224.63 |  |  | 179.27
1994-05-03 | 3224.62 |  |  | 179.25
1994-05-02 | 3224.62 |  |  | 179.25
1994-05-01 | 3224.62 |  |  | 179.16
1994-04-30 | 3224.57 |  |  | 179.15
1994-04-29 | 3224.56 |  |  | 178.75
1994-04-28 | 3224.49 |  |  | 178.72
1994-04-27 | 3224.43 |  |  | 178.81
1994-04-26 | 3224.43 |  |  | 179.12
1994-04-25 | 3224.43 |  |  | 178.99
1994-04-24 | 3224.44 |  |  | 179.23
1994-04-23 | 3224.49 |  |  | 179.21
1994-04-22 | 3224.54 |  |  | 179.27
1994-04-21 | 3224.55 |  |  | 172.75
1994-04-20 | 3224.55 |  |  | 167.98
1994-04-19 | 3224.53 |  |  | 156.27
1994-04-18 | 3224.49 |  |  | 150.08
1994-04-17 | 3224.43 |  |  | 144.78
1994-04-16 | 3224.35 |  |  | 142.72
1994-04-15 | 3224.27 |  |  | 135.86
1994-04-14 | 3224.16 |  |  | 126.91
1994-04-13 | 3224.05 |  |  | 126.91
1994-04-12 | 3223.94 |  |  | 126.92
1994-04-11 | 3223.81 |  |  | 126.91
1994-04-10 | 3223.65 |  |  | 126.91
1994-04-09 | 3223.49 |  |  | 126.91
1994-04-08 | 3223.32 |  |  | 131.92
1994-04-07 | 3223.15 |  |  | 137.81
1994-04-06 | 3222.98 |  |  | 136.66
1994-04-05 | 3222.79 |  |  | 136.57
1994-04-04 | 3222.56 |  |  | 136.57
1994-04-03 | 3222.3 |  |  | 136.57
1994-04-02 | 3221.93 |  |  | 136.57
1994-04-01 | 3221.56 |  |  | 136.57
1994-03-31 | 3221.21 |  |  | 136.57
1994-03-30 | 3220.9 |  |  | 110.1
1994-03-29 | 3220.7 |  |  | 97.56
1994-03-28 | 3220.54 |  |  | 77.42
1994-03-27 | 3220.42 |  |  | 67.04
1994-03-26 | 3220.32 |  |  | 66.96
1994-03-25 | 3220.21 |  |  | 67.02
1994-03-24 | 3220.14 |  |  | 66.92
1994-03-23 | 3220.05 |  |  | 66.99
1994-03-22 | 3219.92 |  |  | 66.91
1994-03-21 | 3219.78 |  |  | 67
1994-03-20 | 3219.62 |  |  | 66.87
1994-03-19 | 3219.43 |  |  | 66.87
1994-03-18 | 3219.21 |  |  | 66.9
1994-03-17 | 3218.97 |  |  | 66.87
1994-03-16 | 3218.68 |  |  | 68.26
1994-03-15 | 3218.33 |  |  | 71.35
1994-03-14 | 3218.06 |  |  | 70.98
1994-03-13 | 3215.09 |  |  | 70.74
1994-03-12 | 3215.09 |  |  | 70.23
1994-03-11 | 3215.09 |  |  | 70.21
1994-03-10 | 3215.09 |  |  | 70.21
1994-03-09 | 3215.09 |  |  | 70.21
1994-03-08 | 3215.09 |  |  | 70.21
1994-03-07 | 3215.09 |  |  | 70.21
1994-03-06 | 3215.09 |  |  | 70.21
1994-03-05 | 3215.09 |  |  | 70.21
1994-03-04 | 3215.09 |  |  | 70.21
1994-03-03 | 3214.6 |  |  | 70.27
1994-03-02 | 3214.06 |  |  | 70.36
1994-03-01 | 3213.8 |  |  | 70.21
1994-02-28 | 3213.46 |  |  | 78.85
1994-02-27 | 3213.09 |  |  | 88.31
1994-02-26 | 3212.77 |  |  | 88.31
1994-02-25 | 3212.66 |  |  | 88.28
1994-02-24 | 3212.62 |  |  | 88.31
1994-02-23 | 3212.6 |  |  | 88.12
1994-02-22 | 3212.58 |  |  | 87.85
1994-02-21 | 3212.57 |  |  | 88.29
1994-02-20 | 3212.55 |  |  | 87.92
1994-02-19 | 3212.53 |  |  | 87.82
1994-02-18 | 3212.52 |  |  | 87.57
1994-02-17 | 3212.52 |  |  | 87.91
1994-02-16 | 3212.48 |  |  | 87.61
1994-02-15 | 3212.48 |  |  | 91.87
1994-02-14 | 3212.52 |  |  | 96.12
1994-02-13 | 3212.52 |  |  | 96.09
1994-02-12 | 3212.53 |  |  | 95.92
1994-02-11 | 3212.54 |  |  | 96.08
1994-02-10 | 3212.54 |  |  | 96.14
1994-02-09 | 3212.54 |  |  | 95.47
1994-02-08 | 3212.54 |  |  | 95.25
1994-02-07 | 3212.54 |  |  | 96.14
1994-02-06 | 3212.54 |  |  | 95.62
1994-02-05 | 3212.55 |  |  | 95.09
1994-02-04 | 3212.55 |  |  | 95.29
1994-02-03 | 3212.6 |  |  | 94.35
1994-02-02 | 3212.61 |  |  | 93.71
1994-02-01 | 3212.61 |  |  | 93.64
1994-01-31 | 3212.61 |  |  | 93.65
1994-01-30 | 3212.59 |  |  | 94.05
1994-01-29 | 3212.59 |  |  | 93.71
1994-01-28 | 3212.59 |  |  | 93.99
1994-01-27 | 3212.55 |  |  | 93.62
1994-01-26 | 3212.55 |  |  | 93.53
1994-01-25 | 3212.55 |  |  | 93.56
1994-01-24 | 3212.55 |  |  | 94.17
1994-01-23 | 3212.54 |  |  | 94.14
1994-01-22 | 3212.52 |  |  | 93.74
1994-01-21 | 3212.52 |  |  | 90.33
1994-01-20 | 3212.48 |  |  | 85.76
1994-01-19 | 3212.46 |  |  | 85.76
1994-01-18 | 3212.44 |  |  | 85.76
1994-01-17 | 3212.42 |  |  | 85.76
1994-01-16 | 3212.39 |  |  | 85.76
1994-01-15 | 3212.34 |  |  | 85.76
1994-01-14 | 3212.32 |  |  | 85.76
1994-01-13 | 3212.28 |  |  | 85.76
1994-01-12 | 3212.25 |  |  | 81.85
1994-01-11 | 3212.21 |  |  | 77.17
1994-01-10 | 3212.16 |  |  | 77.17
1994-01-09 | 3212.12 |  |  | 77.17
1994-01-08 | 3212.05 |  |  | 77.17
1994-01-07 | 3211.99 |  |  | 77.16
1994-01-06 | 3211.86 |  |  | 76.79
1994-01-05 | 3211.68 |  |  | 75.99
1994-01-04 | 3211.57 |  |  | 75.92
1994-01-03 | 3211.56 |  |  | 75.32
1994-01-02 | 3211.34 |  |  | 74.81
1994-01-01 | 3211.3 |  |  | 74.8
1993-12-31 | 3211.29 |  |  | 74.81
1993-12-30 | 3211.28 |  |  | 74.75
1993-12-29 | 3211.27 |  |  | 74.74
1993-12-28 | 3211.24 |  |  | 74.61
1993-12-27 | 3211.23 |  |  | 74.51
1993-12-26 | 3211.22 |  |  | 74.22
1993-12-25 | 3211.22 |  |  | 73.69
1993-12-24 | 3211.21 |  |  | 73.66
1993-12-23 | 3211.2 |  |  | 73.65
1993-12-22 | 3211.2 |  |  | 73.65
1993-12-21 | 3211.2 |  |  | 73.68
1993-12-20 | 3211.2 |  |  | 73.68
1993-12-19 | 3211.19 |  |  | 73.88
1993-12-18 | 3211.19 |  |  | 73.72
1993-12-17 | 3211.16 |  |  | 73.65
1993-12-16 | 3211.08 |  |  | 73.66
1993-12-15 | 3211.06 |  |  | 73.71
1993-12-14 | 3211.02 |  |  | 73.74
1993-12-13 | 3211 |  |  | 73.88
1993-12-12 | 3210.87 |  |  | 73.72
1993-12-11 | 3210.7 |  |  | 73.75
1993-12-10 | 3210.63 |  |  | 73.89
1993-12-09 | 3210.6 |  |  | 73.85
1993-12-08 | 3210.54 |  |  | 73.71
1993-12-07 | 3210.5 |  |  | 73.68
1993-12-06 | 3210.46 |  |  | 73.66
1993-12-05 | 3210.44 |  |  | 73.65
1993-12-04 | 3210.44 |  |  | 73.66
1993-12-03 | 3210.43 |  |  | 70.76
1993-12-02 | 3210.4 |  |  | 67.98
1993-12-01 | 3210.38 |  |  | 68.84
1993-11-30 | 3210.35 |  |  | 78.41
1993-11-29 | 3210.42 |  |  | 90.9
1993-11-28 | 3210.43 |  |  | 90.9
1993-11-27 | 3210.47 |  |  | 90.89
1993-11-26 | 3210.48 |  |  | 90.8
1993-11-25 | 3210.51 |  |  | 90.87
1993-11-24 | 3210.54 |  |  | 91.62
1993-11-23 | 3210.56 |  |  | 92.21
1993-11-22 | 3210.56 |  |  | 92.21
1993-11-21 | 3210.56 |  |  | 92.21
1993-11-20 | 3210.58 |  |  | 75.97
1993-11-19 | 3210.58 |  |  | 73.01
1993-11-18 | 3210.62 |  |  | 73.63
1993-11-17 | 3210.62 |  |  | 73.65
1993-11-16 | 3210.62 |  |  | 73.59
1993-11-15 | 3210.62 |  |  | 73.22
1993-11-14 | 3210.63 |  |  | 73.1
1993-11-13 | 3210.63 |  |  | 73.42
1993-11-12 | 3210.63 |  |  | 73.2
1993-11-11 | 3210.66 |  |  | 73.13
1993-11-10 | 3210.66 |  |  | 73.38
1993-11-09 | 3210.66 |  |  | 73.26
1993-11-08 | 3210.67 |  |  | 73.22
1993-11-07 | 3210.67 |  |  | 73.38
1993-11-06 | 3210.67 |  |  | 73.28
1993-11-05 | 3210.67 |  |  | 72.86
1993-11-04 | 3210.7 |  |  | 73.31
1993-11-03 | 3210.7 |  |  | 73.1
1993-11-02 | 3210.7 |  |  | 72.49
1993-11-01 | 3210.7 |  |  | 72.49
1993-10-31 | 3210.7 |  |  | 72.76
1993-10-30 | 3210.69 |  |  | 72.53
1993-10-29 | 3210.69 |  |  | 72.49
1993-10-28 | 3210.69 |  |  | 72.49
1993-10-27 | 3210.69 |  |  | 72.49
1993-10-26 | 3210.69 |  |  | 72.49
1993-10-25 | 3210.69 |  |  | 72.49
1993-10-24 | 3210.69 |  |  | 72.49
1993-10-23 | 3210.69 |  |  | 72.49
1993-10-22 | 3210.69 |  |  | 74.56
1993-10-21 | 3210.69 |  |  | 78.37
1993-10-20 | 3210.69 |  |  | 78.37
1993-10-19 | 3210.65 |  |  | 90.95
1993-10-18 | 3210.65 |  |  | 125.4
1993-10-17 | 3210.75 |  |  | 153.57
1993-10-16 | 3210.79 |  |  | 153.57
1993-10-15 | 3210.85 |  |  | 162.61
1993-10-14 | 3210.96 |  |  | 175.46
1993-10-13 | 3211.02 |  |  | 175.46
1993-10-12 | 3211.08 |  |  | 191.78
1993-10-11 | 3211.23 |  |  | 201.63
1993-10-10 | 3211.36 |  |  | 201.63
1993-10-09 | 3211.51 |  |  | 201.65
1993-10-08 | 3211.64 |  |  | 201.63
1993-10-07 | 3211.79 |  |  | 201.63
1993-10-06 | 3211.99 |  |  | 201.67
1993-10-05 | 3212.15 |  |  | 201.63
1993-10-04 | 3212.3 |  |  | 201.63
1993-10-03 | 3212.45 |  |  | 201.63
1993-10-02 | 3212.64 |  |  | 201.63
1993-10-01 | 3212.78 |  |  | 201.63
1993-09-30 | 3212.92 |  |  | 201.63
1993-09-29 | 3213.1 |  |  | 201.63
1993-09-28 | 3213.24 |  |  | 201.63
1993-09-27 | 3213.39 |  |  | 201.63
1993-09-26 | 3213.55 |  |  | 201.63
1993-09-25 | 3213.7 |  |  | 201.63
1993-09-24 | 3213.82 |  |  | 206.73
1993-09-23 | 3213.99 |  |  | 213.2
1993-09-22 | 3214.17 |  |  | 209.88
1993-09-21 | 3214.36 |  |  | 209.41
1993-09-20 | 3214.5 |  |  | 209.47
1993-09-19 | 3214.69 |  |  | 209.45
1993-09-18 | 3214.9 |  |  | 209.41
1993-09-17 | 3215.09 |  |  | 209.64
1993-09-16 | 3215.3 |  |  | 209.86
1993-09-15 | 3215.5 |  |  | 210.15
1993-09-14 | 3215.71 |  |  | 209.99
1993-09-13 | 3215.88 |  |  | 223.16
1993-09-12 | 3217.12 |  |  | 238.5
1993-09-11 | 3216.86 |  |  | 238.65
1993-09-10 | 3216.64 |  |  | 261.83
1993-09-09 | 3216.81 |  |  | 321.21
1993-09-08 | 3217.12 |  |  | 368.08
1993-09-07 | 3217.46 |  |  | 368.1
1993-09-06 | 3217.79 |  |  | 368.34
1993-09-05 | 3218.07 |  |  | 368.73
1993-09-04 | 3218.4 |  |  | 368.73
1993-09-03 | 3218.74 |  |  | 368.97
1993-09-02 | 3219.02 |  |  | 369.62
1993-09-01 | 3219.33 |  |  | 370.35
1993-08-31 | 3219.65 |  |  | 370.56
1993-08-30 | 3219.94 |  |  | 370.42
1993-08-29 | 3220.27 |  |  | 370.78
1993-08-28 | 3220.58 |  |  | 370.9
1993-08-27 | 3220.86 |  |  | 370.9
1993-08-26 | 3221.18 |  |  | 370.9
1993-08-25 | 3221.47 |  |  | 370.9
1993-08-24 | 3221.78 |  |  | 370.93
1993-08-23 | 3222.11 |  |  | 370.96
1993-08-22 | 3222.38 |  |  | 370.93
1993-08-21 | 3222.55 |  |  | 370.9
1993-08-20 | 3222.8 |  |  | 371.21
1993-08-19 | 3223.05 |  |  | 370.99
1993-08-18 | 3223.29 |  |  | 370.9
1993-08-17 | 3223.58 |  |  | 370.9
1993-08-16 | 3223.85 |  |  | 371.02
1993-08-15 | 3224.18 |  |  | 371.39
1993-08-14 | 3224.49 |  |  | 371.14
1993-08-13 | 3224.79 |  |  | 371.27
1993-08-12 | 3225.11 |  |  | 371.3
1993-08-11 | 3225.42 |  |  | 371.64
1993-08-10 | 3225.73 |  |  | 371.57
1993-08-09 | 3226.05 |  |  | 371.9
1993-08-08 | 3226.36 |  |  | 371.99
1993-08-07 | 3226.65 |  |  | 372.78
1993-08-06 | 3226.93 |  |  | 373.23
1993-08-05 | 3227.25 |  |  | 373.32
1993-08-04 | 3227.55 |  |  | 373.57
1993-08-03 | 3227.82 |  |  | 373.63
1993-08-02 | 3228.08 |  |  | 373.78
1993-08-01 | 3228.31 |  |  | 373.81
1993-07-31 | 3228.57 |  |  | 373.81
1993-07-30 | 3228.83 |  |  | 373.81
1993-07-29 | 3229.1 |  |  | 374.09
1993-07-28 | 3229.41 |  |  | 374.98
1993-07-27 | 3229.68 |  |  | 375.55
1993-07-26 | 3229.88 |  |  | 376.64
1993-07-25 | 3230.1 |  |  | 376.73
1993-07-24 | 3230.38 |  |  | 376.89
1993-07-23 | 3230.62 |  |  | 378.54
1993-07-22 | 3230.88 |  |  | 379.61
1993-07-21 | 3231.08 |  |  | 379.67
1993-07-20 | 3231.31 |  |  | 358.23
1993-07-19 | 3231.57 |  |  | 327.15
1993-07-18 | 3231.78 |  |  | 327.15
1993-07-17 | 3232.01 |  |  | 327.21
1993-07-16 | 3232.24 |  |  | 304.54
1993-07-15 | 3232.43 |  |  | 272.04
1993-07-14 | 3232.61 |  |  | 273.24
1993-07-13 | 3232.78 |  |  | 273.31
1993-07-12 | 3233 |  |  | 273
1993-07-11 | 3233.21 |  |  | 273
1993-07-10 | 3233.4 |  |  | 273
1993-07-09 | 3233.56 |  |  | 261.79
1993-07-08 | 3233.76 |  |  | 242.73
1993-07-07 | 3233.89 |  |  | 262
1993-07-06 | 3233.95 |  |  | 262.08
1993-07-05 | 3234.1 |  |  | 262.7
1993-07-04 | 3234.24 |  |  | 263.19
1993-07-03 | 3234.37 |  |  | 264.12
1993-07-02 | 3234.5 |  |  | 264.23
1993-07-01 | 3234.68 |  |  | 264.27
1993-06-30 | 3234.82 |  |  | 220.04
1993-06-29 | 3234.94 |  |  | 196.25
1993-06-28 | 3235.01 |  |  | 199.21
1993-06-27 | 3235.12 |  |  | 202.73
1993-06-26 | 3235.22 |  |  | 206.54
1993-06-25 | 3235.28 |  |  | 209.9
1993-06-24 | 3235.35 |  |  | 213.41
1993-06-23 | 3235.41 |  |  | 218.01
1993-06-22 | 3235.5 |  |  | 223.93
1993-06-21 | 3235.62 |  |  | 231.28
1993-06-20 | 3235.73 |  |  | 236.39
1993-06-19 | 3235.82 |  |  | 242.11
1993-06-18 | 3235.85 |  |  | 262.61
1993-06-17 | 3235.93 |  |  | 294.62
1993-06-16 | 3235.96 |  |  | 300.35
1993-06-15 | 3236.03 |  |  | 307.87
1993-06-14 | 3236.13 |  |  | 313.61
1993-06-13 | 3236.14 |  |  | 317.77
1993-06-12 | 3236.14 |  |  | 319.27
1993-06-11 | 3236.14 |  |  | 320.26
1993-06-10 | 3236.12 |  |  | 318.76
1993-06-09 | 3236.09 |  |  | 312.17
1993-06-08 | 3235.98 |  |  | 295.93
1993-06-07 | 3235.82 |  |  | 279.25
1993-06-06 | 3235.59 |  |  | 260.76
1993-06-05 | 3235.29 |  |  | 245.37
1993-06-04 | 3235.16 |  |  | 238.34
1993-06-03 | 3235.03 |  |  | 232.21
1993-06-02 | 3234.92 |  |  | 227.91
1993-06-01 | 3234.85 |  |  | 226.33
1993-05-31 | 3234.75 |  |  | 226.02
1993-05-30 | 3234.63 |  |  | 225.11
1993-05-29 | 3234.5 |  |  | 224.48
1993-05-28 | 3234.36 |  |  | 224.28
1993-05-27 | 3234.18 |  |  | 224.36
1993-05-26 | 3234.1 |  |  | 242.59
1993-05-25 | 3234.07 |  |  | 286.62
1993-05-24 | 3234.06 |  |  | 365.35
1993-05-23 | 3234.14 |  |  | 425.26
1993-05-22 | 3234.15 |  |  | 425.08
1993-05-21 | 3234.15 |  |  | 570.13
1993-05-20 | 3234.27 |  |  | 819.87
1993-05-19 | 3234.45 |  |  | 1062.5
1993-05-18 | 3234.8 |  |  | 1150.07
1993-05-17 | 3235.06 |  |  | 1206.56
1993-05-16 | 3235.33 |  |  | 1296.9
1993-05-15 | 3235.6 |  |  | 1314.66
1993-05-14 | 3235.77 |  |  | 1369.94
1993-05-13 | 3235.85 |  |  | 1446.41
1993-05-12 | 3235.91 |  |  | 1452.19
1993-05-11 | 3236.01 |  |  | 1511.87
1993-05-10 | 3236.17 |  |  | 1602.21
1993-05-09 | 3236.33 |  |  | 1610.97
1993-05-08 | 3236.34 |  |  | 1611.06
1993-05-07 | 3236.31 |  |  | 1608.6
1993-05-06 | 3236.13 |  |  | 1594.61
1993-05-05 | 3236.01 |  |  | 1573.97
1993-05-04 | 3235.72 |  |  | 1529.14
1993-05-03 | 3235.1 |  |  | 1496.49
1993-05-02 | 3234.79 |  |  | 1489.34
1993-05-01 | 3234.52 |  |  | 1487.06
1993-04-30 | 3234.27 |  |  | 1538.21
1993-04-29 | 3234.04 |  |  | 1664.87
1993-04-28 | 3233.9 |  |  | 1778.42
1993-04-27 | 3233.89 |  |  | 1906.83
1993-04-26 | 3233.83 |  |  | 1983.18
1993-04-25 | 3233.83 |  |  | 2068.75
1993-04-24 | 3233.88 |  |  | 2292.95
1993-04-23 | 3234.05 |  |  | 2438.54
1993-04-22 | 3234.23 |  |  | 2629.75
1993-04-21 | 3234.49 |  |  | 2823.86
1993-04-20 | 3234.95 |  |  | 2947.34
1993-04-19 | 3235.67 |  |  | 2972.11
1993-04-18 | 3236.24 |  |  | 3010.03
1993-04-17 | 3236.77 |  |  | 2987.06
1993-04-16 | 3237.54 |  |  | 2983.69
1993-04-15 | 3238.24 |  |  | 2970.03
1993-04-14 | 3239.06 |  |  | 2944.24
1993-04-13 | 3239.77 |  |  | 2935.97
1993-04-12 | 3240.53 |  |  | 2936.59
1993-04-11 | 3241.08 |  |  | 2979.81
1993-04-10 | 3241.46 |  |  | 3014.67
1993-04-09 | 3241.71 |  |  | 3070.5
1993-04-08 | 3241.85 |  |  | 3128.49
1993-04-07 | 3242.09 |  |  | 3151.4
1993-04-06 | 3242.37 |  |  | 3178.07
1993-04-05 | 3242.42 |  |  | 3174.04
1993-04-04 | 3242.11 |  |  | 3250.84
1993-04-03 | 3240.94 |  |  | 3153.29
1993-04-02 | 3240.41 |  |  | 3218.03
1993-04-01 | 3239.88 |  |  | 3142.95
1993-03-31 | 3239.72 |  |  | 3097.44
1993-03-30 | 3240.1 |  |  | 3121.71
1993-03-29 | 3240.26 |  |  | 3140.67
1993-03-28 | 3240.41 |  |  | 3164.94
1993-03-27 | 3240.39 |  |  | 3166.22
1993-03-26 | 3240.16 |  |  | 3102.02
1993-03-25 | 3239.66 |  |  | 3096.53
1993-03-24 | 3238.01 |  |  | 3116.96
1993-03-23 | 3234.57 |  |  | 3054.75
1993-03-22 | 3232.52 |  |  | 2228.57
1993-03-21 | 3230.83 |  |  | 1661.92
1993-03-20 | 3227.92 |  |  | 1259.33
1993-03-19 | 3223.93 |  |  | 730.38
1993-03-18 | 3217.82 |  |  | 337.12
1993-03-17 | 3210.87 |  |  | 200.45
1993-03-16 | 3204.28 |  |  | 85.67
1993-03-15 | 3199 |  |  | 33.19
1993-03-14 | 3195.14 |  |  | 32.84
1993-03-13 | 3193.8 |  |  | 32.5
1993-03-12 | 3192.34 |  |  | 32.5
1993-03-11 | 3190.7 |  |  | 32.04
1993-03-10 | 3188.82 |  |  | 31.76
1993-03-09 | 3187.04 |  |  | 31.76
1993-03-08 | 3185.74 |  |  | 31.4
1993-03-07 | 3184.51 |  |  | 31.03
1993-03-06 | 3183.49 |  |  | 71.51
1993-03-05 | 3183.02 |  |  | 31.03
1993-03-04 | 3182.68 |  |  | 31.03
1993-03-03 | 3182.35 |  |  | 31.03
1993-03-02 | 3182.08 |  |  | 30.96
1993-03-01 | 3181.87 |  |  | 30.7
1993-02-28 | 3181.7 |  |  | 30.55
1993-02-27 | 3181.5 |  |  | 30.7
1993-02-26 | 3181.35 |  |  | 30.82
1993-02-25 | 3181.13 |  |  | 30.6
1993-02-24 | 3180.9 |  |  | 30.91
1993-02-23 | 3180.69 |  |  | 30.61
1993-02-22 | 3180.48 |  |  | 30.31
1993-02-21 | 3180.23 |  |  | 30.33
1993-02-20 | 3179.95 |  |  | 30.61
1993-02-19 | 3179.64 |  |  | 31.02
1993-02-18 | 3179.37 |  |  | 31.03
1993-02-17 | 3179.13 |  |  | 30.81
1993-02-16 | 3178.9 |  |  | 30.72
1993-02-15 | 3178.59 |  |  | 31.03
1993-02-14 | 3178.2 |  |  | 31.03
1993-02-13 | 3177.85 |  |  | 30.56
1993-02-12 | 3177.46 |  |  | 30.31
1993-02-11 | 3177.17 |  |  | 30.31
1993-02-10 | 3176.9 |  |  | 30.31
1993-02-09 | 3176.63 |  |  | 30.31
1993-02-08 | 3176.42 |  |  | 30.31
1993-02-07 | 3176.19 |  |  | 30.31
1993-02-06 | 3176.02 |  |  | 30.31
1993-02-05 | 3175.86 |  |  | 30.31
1993-02-04 | 3175.64 |  |  | 30.31
1993-02-03 | 3175.4 |  |  | 30.3
1993-02-02 | 3175.2 |  |  | 30.29
1993-02-01 | 3175.04 |  |  | 30.31
1993-01-31 | 3174.92 |  |  | 30.27
1993-01-30 | 3174.69 |  |  | 30.24
1993-01-29 | 3174.43 |  |  | 30.12
1993-01-28 | 3174.22 |  |  | 29.81
1993-01-27 | 3174.03 |  |  | 29.62
1993-01-26 | 3173.73 |  |  | 29.61
1993-01-25 | 3173.45 |  |  | 29.6
1993-01-24 | 3173.14 |  |  | 29.6
1993-01-23 | 3172.83 |  |  | 29.62
1993-01-22 | 3172.58 |  |  | 29.6
1993-01-21 | 3172.28 |  |  | 29.68
1993-01-20 | 3172.02 |  |  | 29.77
1993-01-19 | 3171.87 |  |  | 29.69
1993-01-18 | 3171.67 |  |  | 29.6
1993-01-17 | 3171.56 |  |  | 29.6
1993-01-16 | 3171.43 |  |  | 29.6
1993-01-15 | 3171.29 |  |  | 29.6
1993-01-14 | 3171.19 |  |  | 29.6
1993-01-13 | 3171.02 |  |  | 29.6
1993-01-12 | 3170.84 |  |  | 29.37
1993-01-11 | 3170.71 |  |  | 29.3
1993-01-10 | 3170.64 |  |  | 29.6
1993-01-09 | 3170.54 |  |  | 29.6
1993-01-08 | 3170.44 |  |  | 29.61
1993-01-07 | 3170.31 |  |  | 29.6
1993-01-06 | 3170.19 |  |  | 29.62
1993-01-05 | 3170.03 |  |  | 30.05
1993-01-04 | 3169.86 |  |  | 29.99
1993-01-03 | 3169.68 |  |  | 29.75
1993-01-02 | 3169.51 |  |  | 30.04
1993-01-01 | 3169.43 |  |  | 30.3
1992-12-31 | 3169.24 |  |  | 30.3
1992-12-30 | 3169.09 |  |  | 30.27
1992-12-29 | 3168.94 |  |  | 30.31
1992-12-28 | 3168.78 |  |  | 30.31
1992-12-27 | 3168.65 |  |  | 30.3
1992-12-26 | 3168.52 |  |  | 30.31
1992-12-25 | 3168.42 |  |  | 30.3
1992-12-24 | 3168.32 |  |  | 30.31
1992-12-23 | 3168.2 |  |  | 30.3
1992-12-22 | 3168.06 |  |  | 30.28
1992-12-21 | 3167.89 |  |  | 30.16
1992-12-20 | 3167.79 |  |  | 29.99
1992-12-19 | 3167.67 |  |  | 29.88
1992-12-18 | 3167.53 |  |  | 29.74
1992-12-17 | 3167.38 |  |  | 29.66
1992-12-16 | 3167.27 |  |  | 29.82
1992-12-15 | 3167.11 |  |  | 29.7
1992-12-14 | 3166.97 |  |  | 29.62
1992-12-13 | 3166.82 |  |  | 29.6
1992-12-12 | 3166.59 |  |  | 29.6
1992-12-11 | 3166.4 |  |  | 29.6
1992-12-10 | 3166.28 |  |  | 29.6
1992-12-09 | 3166.18 |  |  | 29.6
1992-12-08 | 3166.04 |  |  | 30.59
1992-12-07 | 3166.01 |  |  | 32.5
1992-12-06 | 3165.88 |  |  | 32.49
1992-12-05 | 3165.88 |  |  | 32.48
1992-12-04 | 3165.85 |  |  | 32.49
1992-12-03 | 3165.79 |  |  | 32.5
1992-12-02 | 3165.65 |  |  | 32.5
1992-12-01 | 3165.53 |  |  | 32.5
1992-11-30 | 3165.44 |  |  | 32.5
1992-11-29 | 3165.27 |  |  | 32.5
1992-11-28 | 3165.19 |  |  | 32.5
1992-11-27 | 3165.13 |  |  | 32.5
1992-11-26 | 3165.1 |  |  | 32.5
1992-11-25 | 3164.99 |  |  | 32.5
1992-11-24 | 3164.99 |  |  | 32.5
1992-11-23 | 3164.92 |  |  | 32.5
1992-11-22 | 3164.81 |  |  | 32.5
1992-11-21 | 3164.75 |  |  | 32.59
1992-11-20 | 3164.66 |  |  | 32.5
1992-11-19 | 3164.61 |  |  | 32.5
1992-11-18 | 3164.53 |  |  | 32.5
1992-11-17 | 3164.46 |  |  | 32.5
1992-11-16 | 3164.39 |  |  | 32.5
1992-11-15 | 3164.3 |  |  | 32.5
1992-11-14 | 3164.21 |  |  | 32.5
1992-11-13 | 3164.12 |  |  | 32.5
1992-11-12 | 3164 |  |  | 32.5
1992-11-11 | 3163.92 |  |  | 32.58
1992-11-10 | 3163.82 |  |  | 32.5
1992-11-09 | 3163.74 |  |  | 32.51
1992-11-08 | 3163.65 |  |  | 32.58
1992-11-07 | 3163.57 |  |  | 32.57
1992-11-06 | 3163.5 |  |  | 32.5
1992-11-05 | 3163.41 |  |  | 32.5
1992-11-04 | 3163.32 |  |  | 32.51
1992-11-03 | 3163.24 |  |  | 32.51
1992-11-02 | 3163.12 |  |  | 32.54
1992-11-01 | 3163.06 |  |  | 32.56
1992-10-31 | 3162.92 |  |  | 32.61
1992-10-30 | 3162.83 |  |  | 32.54
1992-10-29 | 3162.72 |  |  | 32.66
1992-10-28 | 3162.36 |  |  | 32.75
1992-10-27 | 3162.34 |  |  | 32.51
1992-10-26 | 3162.33 |  |  | 32.5
1992-10-25 | 3162.32 |  |  | 32.5
1992-10-24 | 3162.31 |  |  | 32.5
1992-10-23 | 3162.31 |  |  | 32.5
1992-10-22 | 3162.3 |  |  | 32.5
1992-10-21 | 3162.29 |  |  | 32.51
1992-10-20 | 3162.28 |  |  | 32.37
1992-10-19 | 3162.28 |  |  | 32.02
1992-10-18 | 3162.28 |  |  | 31.81
1992-10-17 | 3162.28 |  |  | 31.81
1992-10-16 | 3162.28 |  |  | 31.76
1992-10-15 | 3162.28 |  |  | 31.76
1992-10-14 | 3162.28 |  |  | 31.76
1992-10-13 | 3162.28 |  |  | 30.55
1992-10-12 | 3162.28 |  |  | 29.74
1992-10-11 | 3162.28 |  |  | 29.7
1992-10-10 | 3162.28 |  |  | 29.6
1992-10-09 | 3162.28 |  |  | 29.6
1992-10-08 | 3162.28 |  |  | 29.6
1992-10-07 | 3162.28 |  |  | 30.64
1992-10-06 | 3162.28 |  |  | 48.51
1992-10-05 | 3162.46 |  |  | 86.12
1992-10-04 | 3162.61 |  |  | 107.34
1992-10-03 | 3162.77 |  |  | 107.34
1992-10-02 | 3163 |  |  | 107.57
1992-10-01 | 3163.15 |  |  | 107.46
1992-09-30 | 3163.41 |  |  | 107.44
1992-09-29 | 3163.63 |  |  | 107.37
1992-09-28 | 3163.76 |  |  | 107.35
1992-09-27 | 3164.02 |  |  | 107.35
1992-09-26 | 3164.23 |  |  | 107.44
1992-09-25 | 3164.46 |  |  | 107.98
1992-09-24 | 3164.71 |  |  | 108.64
1992-09-23 | 3164.97 |  |  | 108.65
1992-09-22 | 3165.23 |  |  | 107.98
1992-09-21 | 3165.46 |  |  | 107.44
1992-09-20 | 3165.7 |  |  | 108.04
1992-09-19 | 3165.95 |  |  | 107.95
1992-09-18 | 3166.19 |  |  | 107.7
1992-09-17 | 3166.43 |  |  | 109.13
1992-09-16 | 3166.68 |  |  | 110.23
1992-09-15 | 3166.9 |  |  | 110.23
1992-09-14 | 3167.12 |  |  | 110.23
1992-09-13 | 3167.41 |  |  | 110.23
1992-09-12 | 3167.62 |  |  | 96.9
1992-09-11 | 3167.83 |  |  | 110.46
1992-09-10 | 3168.08 |  |  | 137.95
1992-09-09 | 3168.37 |  |  | 143.23
1992-09-08 | 3168.69 |  |  | 143.23
1992-09-07 | 3169 |  |  | 143.23
1992-09-06 | 3169.29 |  |  | 152.02
1992-09-05 | 3169.61 |  |  | 155.33
1992-09-04 | 3169.92 |  |  | 155.37
1992-09-03 | 3170.27 |  |  | 155.37
1992-09-02 | 3170.54 |  |  | 155.33
1992-09-01 | 3170.85 |  |  | 155.35
1992-08-31 | 3171.17 |  |  | 155.74
1992-08-30 | 3171.39 |  |  | 155.38
1992-08-29 | 3171.69 |  |  | 139.93
1992-08-28 | 3172.02 |  |  | 136.59
1992-08-27 | 3172.28 |  |  | 120.16
1992-08-26 | 3172.51 |  |  | 114.66
1992-08-25 | 3172.73 |  |  | 114.65
1992-08-24 | 3172.96 |  |  | 136.27
1992-08-23 | 3173.22 |  |  | 178.08
1992-08-22 | 3173.56 |  |  | 201.47
1992-08-21 | 3173.96 |  |  | 201.47
1992-08-20 | 3174.31 |  |  | 201.47
1992-08-19 | 3174.74 |  |  | 201.47
1992-08-18 | 3175.12 |  |  | 201.47
1992-08-17 | 3175.47 |  |  | 216.25
1992-08-16 | 3175.85 |  |  | 228.16
1992-08-15 | 3176.29 |  |  | 228.24
1992-08-14 | 3176.61 |  |  | 228.24
1992-08-13 | 3176.99 |  |  | 228.24
1992-08-12 | 3177.11 |  |  | 228.24
1992-08-11 | 3177.48 |  |  | 228.24
1992-08-10 | 3177.87 |  |  | 228.3
1992-08-09 | 3178.21 |  |  | 228.93
1992-08-08 | 3178.6 |  |  | 230.21
1992-08-07 | 3178.97 |  |  | 230.29
1992-08-06 | 3179.36 |  |  | 230.27
1992-08-05 | 3179.77 |  |  | 230.27
1992-08-04 | 3180.14 |  |  | 230.53
1992-08-03 | 3180.51 |  |  | 210.26
1992-08-02 | 3180.87 |  |  | 205.15
1992-08-01 | 3181.19 |  |  | 205.15
1992-07-31 | 3181.5 |  |  | 205.17
1992-07-30 | 3181.83 |  |  | 205.17
1992-07-29 | 3182.14 |  |  | 205.47
1992-07-28 | 3182.45 |  |  | 206.87
1992-07-27 | 3182.77 |  |  | 207
1992-07-26 | 3183.07 |  |  | 207
1992-07-25 | 3183.37 |  |  | 207
1992-07-24 | 3183.62 |  |  | 219.72
1992-07-23 | 3183.93 |  |  | 228.2
1992-07-22 | 3184.21 |  |  | 228.24
1992-07-21 | 3184.52 |  |  | 228.24
1992-07-20 | 3184.89 |  |  | 228.39
1992-07-19 | 3185.21 |  |  | 229.2
1992-07-18 | 3185.56 |  |  | 215.06
1992-07-17 | 3185.85 |  |  | 203.3
1992-07-16 | 3186.16 |  |  | 178.37
1992-07-15 | 3186.39 |  |  | 173.57
1992-07-14 | 3186.69 |  |  | 173.57
1992-07-13 | 3186.92 |  |  | 173.57
1992-07-12 | 3187.16 |  |  | 173.57
1992-07-11 | 3187.44 |  |  | 173.61
1992-07-10 | 3187.67 |  |  | 159.17
1992-07-09 | 3187.88 |  |  | 142.42
1992-07-08 | 3188.07 |  |  | 130.08
1992-07-07 | 3188.25 |  |  | 130.08
1992-07-06 | 3188.42 |  |  | 144.89
1992-07-05 | 3188.61 |  |  | 153.71
1992-07-04 | 3188.78 |  |  | 155.37
1992-07-03 | 3188.95 |  |  | 155.37
1992-07-02 | 3189.21 |  |  | 167.74
1992-07-01 | 3189.4 |  |  | 201.13
1992-06-30 | 3189.65 |  |  | 229.61
1992-06-29 | 3189.92 |  |  | 232.21
1992-06-28 | 3190.25 |  |  | 232.29
1992-06-27 | 3190.57 |  |  | 232.27
1992-06-26 | 3190.9 |  |  | 240.33
1992-06-25 | 3191.24 |  |  | 251.45
1992-06-24 | 3191.56 |  |  | 244.69
1992-06-23 | 3191.9 |  |  | 244.67
1992-06-22 | 3192.27 |  |  | 244.69
1992-06-21 | 3192.58 |  |  | 244.67
1992-06-20 | 3192.89 |  |  | 202.23
1992-06-19 | 3193.15 |  |  | 185.01
1992-06-18 | 3193.38 |  |  | 185.07
1992-06-17 | 3193.66 |  |  | 185.07
1992-06-16 | 3193.86 |  |  | 185.07
1992-06-15 | 3194.1 |  |  | 185.36
1992-06-14 | 3194.32 |  |  | 185.41
1992-06-13 | 3194.59 |  |  | 186.69
1992-06-12 | 3194.82 |  |  | 184.67
1992-06-11 | 3195.14 |  |  | 180.19
1992-06-10 | 3195.35 |  |  | 179.27
1992-06-09 | 3195.58 |  |  | 179.27
1992-06-08 | 3195.85 |  |  | 180
1992-06-07 | 3196.05 |  |  | 180
1992-06-06 | 3196.3 |  |  | 180
1992-06-05 | 3196.52 |  |  | 180
1992-06-04 | 3196.76 |  |  | 181.21
1992-06-03 | 3196.98 |  |  | 181.21
1992-06-02 | 3197.23 |  |  | 181.3
1992-06-01 | 3197.44 |  |  | 181.52
1992-05-31 | 3197.72 |  |  | 181
1992-05-30 | 3197.92 |  |  | 181
1992-05-29 | 3198.16 |  |  | 181
1992-05-28 | 3198.41 |  |  | 181
1992-05-27 | 3198.61 |  |  | 181
1992-05-26 | 3198.84 |  |  | 181
1992-05-25 | 3199.09 |  |  | 181
1992-05-24 | 3199.28 |  |  | 181
1992-05-23 | 3199.47 |  |  | 182
1992-05-22 | 3199.67 |  |  | 183
1992-05-21 | 3199.89 |  |  | 183
1992-05-20 | 3200.1 |  |  | 183
1992-05-19 | 3200.35 |  |  | 183
1992-05-18 | 3200.59 |  |  | 184
1992-05-17 | 3200.77 |  |  | 185
1992-05-16 | 3201 |  |  | 185
1992-05-15 | 3201.2 |  |  | 184
1992-05-14 | 3201.41 |  |  | 184
1992-05-13 | 3201.62 |  |  | 185
1992-05-12 | 3201.83 |  |  | 184
1992-05-11 | 3202.01 |  |  | 183
1992-05-10 | 3202.24 |  |  | 183
1992-05-09 | 3202.44 |  |  | 183
1992-05-08 | 3202.66 |  |  | 182
1992-05-07 | 3202.86 |  |  | 178
1992-05-06 | 3203.04 |  |  | 174
1992-05-05 | 3203.18 |  |  | 168
1992-05-04 | 3203.38 |  |  | 168
1992-05-03 | 3203.53 |  |  | 168
1992-05-02 | 3203.64 |  |  | 168
1992-05-01 | 3203.78 |  |  | 168
1992-04-30 | 3203.91 |  |  | 167.98
1992-04-29 | 3204.07 |  |  | 167.98
1992-04-28 | 3204.21 |  |  | 157.57
1992-04-27 | 3204.3 |  |  | 140.93
1992-04-26 | 3204.38 |  |  | 140.51
1992-04-25 | 3204.44 |  |  | 139.88
1992-04-24 | 3204.46 |  |  | 139.88
1992-04-23 | 3204.53 |  |  | 139.88
1992-04-22 | 3204.61 |  |  | 139.88
1992-04-21 | 3204.62 |  |  | 139.88
1992-04-20 | 3204.62 |  |  | 139.88
1992-04-19 | 3204.61 |  |  | 62.77
1992-04-18 | 3204.42 |  |  | 42.66
1992-04-17 | 3204.3 |  |  | 41.27
1992-04-16 | 3204.14 |  |  | 38.33
1992-04-15 | 3203.99 |  |  | 38.38
1992-04-14 | 3203.79 |  |  | 76.3
1992-04-13 | 3203.62 |  |  | 125.34
1992-04-12 | 3203.56 |  |  | 125.34
1992-04-11 | 3203.5 |  |  | 125.34
1992-04-10 | 3203.44 |  |  | 78.25
1992-04-09 | 3203.44 |  |  | 98.38
1992-04-08 | 3203.47 |  |  | 125.34
1992-04-07 | 3203.52 |  |  | 125.34
1992-04-06 | 3203.55 |  |  | 120.59
1992-04-05 | 3203.58 |  |  | 116.14
1992-04-04 | 3203.59 |  |  | 116.14
1992-04-03 | 3203.61 |  |  | 116.14
1992-04-02 | 3203.61 |  |  | 116.14
1992-04-01 | 3203.61 |  |  | 53.59
1992-03-31 | 3203.53 |  |  | 24.89
1992-03-30 | 3203.33 |  |  | 24.89
1992-03-29 | 3203.19 |  |  | 24.89
1992-03-28 | 3203.01 |  |  | 24.89
1992-03-27 | 3202.8 |  |  | 24.89
1992-03-26 | 3202.6 |  |  | 24.89
1992-03-25 | 3202.47 |  |  | 24.89
1992-03-24 | 3202.27 |  |  | 24.88
1992-03-23 | 3202.1 |  |  | 24.86
1992-03-22 | 3201.87 |  |  | 24.84
1992-03-21 | 3201.63 |  |  | 24.76
1992-03-20 | 3201.39 |  |  | 24.69
1992-03-19 | 3201.14 |  |  | 24.7
1992-03-18 | 3200.84 |  |  | 24.54
1992-03-17 | 3200.52 |  |  | 24.52
1992-03-16 | 3200.24 |  |  | 24.52
1992-03-15 | 3199.91 |  |  | 24.52
1992-03-14 | 3199.62 |  |  | 24.52
1992-03-13 | 3199.27 |  |  | 24.45
1992-03-12 | 3198.9 |  |  | 24.14
1992-03-11 | 3198.48 |  |  | 24.1
1992-03-10 | 3198.08 |  |  | 23.87
1992-03-09 | 3197.64 |  |  | 25.81
1992-03-08 | 3197.08 |  |  | 30.31
1992-03-07 | 3196.42 |  |  | 30.31
1992-03-06 | 3195.66 |  |  | 30.31
1992-03-05 | 3195.18 |  |  | 30.31
1992-03-04 | 3194.66 |  |  | 30.31
1992-03-03 | 3194.15 |  |  | 30.31
1992-03-02 | 3193.65 |  |  | 30.31
1992-03-01 | 3193.13 |  |  | 30.31
1992-02-29 | 3192.58 |  |  | 30.31
1992-02-28 | 3192.06 |  |  | 30.31
1992-02-27 | 3191.5 |  |  | 29.93
1992-02-26 | 3190.94 |  |  | 29.87
1992-02-25 | 3190.33 |  |  | 29.64
1992-02-24 | 3189.73 |  |  | 29.54
1992-02-23 | 3189.05 |  |  | 29.15
1992-02-22 | 3188.11 |  |  | 28.9
1992-02-21 | 3186.82 |  |  | 30.41
1992-02-20 | 3185.76 |  |  | 32.5
1992-02-19 | 3184.79 |  |  | 32.5
1992-02-18 | 3184.6 |  |  | 32.5
1992-02-17 | 3184.41 |  |  | 32.5
1992-02-16 | 3184.16 |  |  | 32.5
1992-02-15 | 3183.96 |  |  | 32.5
1992-02-14 | 3183.78 |  |  | 34.05
1992-02-13 | 3183.41 |  |  | 36.64
1992-02-12 | 3183.23 |  |  | 37.46
1992-02-11 | 3183.01 |  |  | 37.46
1992-02-10 | 3182.84 |  |  | 37.46
1992-02-09 | 3182.67 |  |  | 37.46
1992-02-08 | 3182.56 |  |  | 37.46
1992-02-07 | 3182.49 |  |  | 37.46
1992-02-06 | 3182.35 |  |  | 37.46
1992-02-05 | 3182.24 |  |  | 37.46
1992-02-04 | 3182.16 |  |  | 37.46
1992-02-03 | 3182.06 |  |  | 37.46
1992-02-02 | 3181.91 |  |  | 37.46
1992-02-01 | 3181.77 |  |  | 37.46
1992-01-31 | 3181.6 |  |  | 37.47
1992-01-30 | 3181.48 |  |  | 37.46
1992-01-29 | 3181.41 |  |  | 37.46
1992-01-28 | 3181.27 |  |  | 37.46
1992-01-27 | 3181.2 |  |  | 37.46
1992-01-26 | 3181.16 |  |  | 37.46
1992-01-25 | 3181.14 |  |  | 37.46
1992-01-24 | 3181.07 |  |  | 37.46
1992-01-23 | 3180.98 |  |  | 37.46
1992-01-22 | 3180.87 |  |  | 37.46
1992-01-21 | 3180.77 |  |  | 37.46
1992-01-20 | 3180.7 |  |  | 37.46
1992-01-19 | 3180.69 |  |  | 37.46
1992-01-18 | 3180.69 |  |  | 37.5
1992-01-17 | 3180.63 |  |  | 37.46
1992-01-16 | 3180.5 |  |  | 37.46
1992-01-15 | 3180.47 |  |  | 37.46
1992-01-14 | 3180.36 |  |  | 37.46
1992-01-13 | 3180.27 |  |  | 37.46
1992-01-12 | 3180.22 |  |  | 37.46
1992-01-11 | 3180.2 |  |  | 37.76
1992-01-10 | 3180.17 |  |  | 37.52
1992-01-09 | 3179.97 |  |  | 37.46
1992-01-08 | 3179.92 |  |  | 37.47
1992-01-07 | 3179.85 |  |  | 37.46
1992-01-06 | 3179.8 |  |  | 37.46
1992-01-05 | 3179.71 |  |  | 37.46
1992-01-04 | 3179.58 |  |  | 37.46
1992-01-03 | 3179.49 |  |  | 37.46
1992-01-02 | 3179.41 |  |  | 37.04
1992-01-01 | 3179.32 |  |  | 36.73
1991-12-31 | 3179.23 |  |  | 36.73
1991-12-30 | 3179.16 |  |  | 36.73
1991-12-29 | 3179.05 |  |  | 36.73
1991-12-28 | 3178.94 |  |  | 36.73
1991-12-27 | 3178.9 |  |  | 36.73
1991-12-26 | 3178.78 |  |  | 36.73
1991-12-25 | 3178.71 |  |  | 36.73
1991-12-24 | 3178.67 |  |  | 36.73
1991-12-23 | 3178.55 |  |  | 36.73
1991-12-22 | 3178.46 |  |  | 36.73
1991-12-21 | 3178.43 |  |  | 36.73
1991-12-20 | 3178.41 |  |  | 36.73
1991-12-19 | 3178.32 |  |  | 36.73
1991-12-18 | 3178.27 |  |  | 36.73
1991-12-17 | 3178.09 |  |  | 36.73
1991-12-16 | 3177.97 |  |  | 36.73
1991-12-15 | 3177.91 |  |  | 36.73
1991-12-14 | 3177.8 |  |  | 36.73
1991-12-13 | 3177.71 |  |  | 36.73
1991-12-12 | 3177.57 |  |  | 36.73
1991-12-11 | 3177.37 |  |  | 36.73
1991-12-10 | 3177.19 |  |  | 36.73
1991-12-09 | 3176.91 |  |  | 36.43
1991-12-08 | 3176.43 |  |  | 36.01
1991-12-07 | 3175.89 |  |  | 36.01
1991-12-06 | 3175.41 |  |  | 36.04
1991-12-05 | 3175.23 |  |  | 36.01
1991-12-04 | 3175.1 |  |  | 35.44
1991-12-03 | 3174.98 |  |  | 35.29
1991-12-02 | 3174.85 |  |  | 35.29
1991-12-01 | 3174.7 |  |  | 35.29
1991-11-30 | 3174.57 |  |  | 35.41
1991-11-29 | 3174.44 |  |  | 36.97
1991-11-28 | 3174.24 |  |  | 35.96
1991-11-27 | 3173.89 |  |  | 35.29
1991-11-26 | 3173.52 |  |  | 35.44
1991-11-25 | 3173.33 |  |  | 35.38
1991-11-24 | 3173.22 |  |  | 35.4
1991-11-23 | 3173.14 |  |  | 35.31
1991-11-22 | 3173.06 |  |  | 35.29
1991-11-21 | 3172.91 |  |  | 35.29
1991-11-20 | 3172.87 |  |  | 35.29
1991-11-19 | 3172.72 |  |  | 35.29
1991-11-18 | 3172.67 |  |  | 35.29
1991-11-17 | 3172.57 |  |  | 35.29
1991-11-16 | 3172.53 |  |  | 35.3
1991-11-15 | 3172.41 |  |  | 35.29
1991-11-14 | 3172.29 |  |  | 35.29
1991-11-13 | 3172.19 |  |  | 35.6
1991-11-12 | 3172.08 |  |  | 36.01
1991-11-11 | 3171.95 |  |  | 36.01
1991-11-10 | 3171.86 |  |  | 36.01
1991-11-09 | 3171.77 |  |  | 36.01
1991-11-08 | 3171.65 |  |  | 36.01
1991-11-07 | 3171.52 |  |  | 36.01
1991-11-06 | 3171.39 |  |  | 36.01
1991-11-05 | 3171.28 |  |  | 36.01
1991-11-04 | 3171.2 |  |  | 36.01
1991-11-03 | 3171.12 |  |  | 36.01
1991-11-02 | 3171.03 |  |  | 36.01
1991-11-01 | 3170.95 |  |  | 36.01
1991-10-31 | 3170.92 |  |  | 36.01
1991-10-30 | 3170.9 |  |  | 36.01
1991-10-29 | 3170.84 |  |  | 36.01
1991-10-28 | 3170.73 |  |  | 36.01
1991-10-27 | 3170.69 |  |  | 36.01
1991-10-26 | 3170.65 |  |  | 36.01
1991-10-25 | 3170.65 |  |  | 36.11
1991-10-24 | 3170.64 |  |  | 36.01
1991-10-23 | 3170.65 |  |  | 36.01
1991-10-22 | 3170.65 |  |  | 36.01
1991-10-21 | 3170.7 |  |  | 36.01
1991-10-20 | 3170.74 |  |  | 36.01
1991-10-19 | 3170.76 |  |  | 36.01
1991-10-18 | 3170.78 |  |  | 39.83
1991-10-17 | 3170.82 |  |  | 58.92
1991-10-16 | 3170.9 |  |  | 80.13
1991-10-15 | 3171.05 |  |  | 85.76
1991-10-14 | 3171.18 |  |  | 93.3
1991-10-13 | 3171.33 |  |  | 104.49
1991-10-12 | 3171.52 |  |  | 104.49
1991-10-11 | 3171.66 |  |  | 104.49
1991-10-10 | 3171.85 |  |  | 104.49
1991-10-09 | 3172.01 |  |  | 102.11
1991-10-08 | 3172.21 |  |  | 100.32
1991-10-07 | 3172.35 |  |  | 102.51
1991-10-06 | 3172.56 |  |  | 104.49
1991-10-05 | 3172.71 |  |  | 104.49
1991-10-04 | 3172.89 |  |  | 106.24
1991-10-03 | 3173.08 |  |  | 115.44
1991-10-02 | 3173.32 |  |  | 124.81
1991-10-01 | 3173.49 |  |  | 137.41
1991-09-30 | 3173.72 |  |  | 153
1991-09-29 | 3173.97 |  |  | 157
1991-09-28 | 3174.2 |  |  | 157
1991-09-27 | 3174.41 |  |  | 161
1991-09-26 | 3174.66 |  |  | 179
1991-09-25 | 3174.96 |  |  | 190
1991-09-24 | 3175.28 |  |  | 200
1991-09-23 | 3175.59 |  |  | 214
1991-09-22 | 3175.97 |  |  | 222
1991-09-21 | 3176.35 |  |  | 222
1991-09-20 | 3176.73 |  |  | 222
1991-09-19 | 3177.13 |  |  | 222
1991-09-18 | 3177.5 |  |  | 224
1991-09-17 | 3177.86 |  |  | 224
1991-09-16 | 3178.22 |  |  | 224
1991-09-15 | 3178.6 |  |  | 224
1991-09-14 | 3178.96 |  |  | 224
1991-09-13 | 3179.32 |  |  | 224
1991-09-12 | 3179.74 |  |  | 224
1991-09-11 | 3180.1 |  |  | 224
1991-09-10 | 3180.46 |  |  | 224
1991-09-09 | 3180.81 |  |  | 224
1991-09-08 | 3181.17 |  |  | 226
1991-09-07 | 3181.58 |  |  | 226
1991-09-06 | 3181.94 |  |  | 226
1991-09-05 | 3182.3 |  |  | 233
1991-09-04 | 3182.68 |  |  | 249
1991-09-03 | 3183.09 |  |  | 255
1991-09-02 | 3183.47 |  |  | 255
1991-09-01 | 3183.88 |  |  | 255
1991-08-31 | 3184.28 |  |  | 255
1991-08-30 | 3184.69 |  |  | 257
1991-08-29 | 3185.1 |  |  | 258
1991-08-28 | 3185.5 |  |  | 258
1991-08-27 | 3185.99 |  |  | 258
1991-08-26 | 3186.38 |  |  | 258
1991-08-25 | 3186.77 |  |  | 258
1991-08-24 | 3187.2 |  |  | 258
1991-08-23 | 3187.6 |  |  | 248
1991-08-22 | 3188.05 |  |  | 234
1991-08-21 | 3188.4 |  |  | 236
1991-08-20 | 3188.68 |  |  | 247
1991-08-19 | 3189.19 |  |  | 264
1991-08-18 | 3189.35 |  |  | 264
1991-08-17 | 3189.72 |  |  | 264
1991-08-16 | 3190.14 |  |  | 264
1991-08-15 | 3190.52 |  |  | 265
1991-08-14 | 3190.87 |  |  | 266
1991-08-13 | 3191.25 |  |  | 271
1991-08-12 | 3191.65 |  |  | 273
1991-08-11 | 3192.04 |  |  | 273
1991-08-10 | 3192.38 |  |  | 275
1991-08-09 | 3192.74 |  |  | 279
1991-08-08 | 3193.22 |  |  | 285
1991-08-07 | 3193.46 |  |  | 269
1991-08-06 | 3193.83 |  |  | 235
1991-08-05 | 3193.94 |  |  | 218
1991-08-04 | 3194.34 |  |  | 218
1991-08-03 | 3194.56 |  |  | 218
1991-08-02 | 3194.79 |  |  | 218
1991-08-01 | 3195.12 |  |  | 218
1991-07-31 | 3195.38 |  |  | 218
1991-07-30 | 3195.65 |  |  | 218
1991-07-29 | 3195.94 |  |  | 199
1991-07-28 | 3196.21 |  |  | 185
1991-07-27 | 3196.43 |  |  | 185
1991-07-26 | 3196.64 |  |  | 184
1991-07-25 | 3196.91 |  |  | 181
1991-07-24 | 3197.13 |  |  | 181
1991-07-23 | 3197.32 |  |  | 181
1991-07-22 | 3197.54 |  |  | 181
1991-07-21 | 3197.73 |  |  | 181
1991-07-20 | 3197.92 |  |  | 181
1991-07-19 | 3198.13 |  |  | 180
1991-07-18 | 3198.36 |  |  | 179
1991-07-17 | 3198.53 |  |  | 181
1991-07-16 | 3198.7 |  |  | 193
1991-07-15 | 3198.94 |  |  | 203
1991-07-14 | 3199.24 |  |  | 203
1991-07-13 | 3199.5 |  |  | 193
1991-07-12 | 3199.66 |  |  | 181
1991-07-11 | 3199.97 |  |  | 181
1991-07-10 | 3200.23 |  |  | 181
1991-07-09 | 3200.33 |  |  | 181
1991-07-08 | 3200.54 |  |  | 181
1991-07-07 | 3200.66 |  |  | 181
1991-07-06 | 3200.88 |  |  | 181
1991-07-05 | 3201 |  |  | 181
1991-07-04 | 3201.12 |  |  | 181
1991-07-03 | 3201.33 |  |  | 181
1991-07-02 | 3201.47 |  |  | 181
1991-07-01 | 3201.48 |  |  | 181
1991-06-30 | 3201.49 |  |  | 181
1991-06-29 | 3201.62 |  |  | 181
1991-06-28 | 3201.7 |  |  | 178
1991-06-27 | 3201.88 |  |  | 174
1991-06-26 | 3202 |  |  | 174
1991-06-25 | 3202.11 |  |  | 175
1991-06-24 | 3202.24 |  |  | 175
1991-06-23 | 3202.35 |  |  | 175
1991-06-22 | 3202.47 |  |  | 175
1991-06-21 | 3202.57 |  |  | 181
1991-06-20 | 3202.74 |  |  | 191
1991-06-19 | 3202.86 |  |  | 192
1991-06-18 | 3203.07 |  |  | 193
1991-06-17 | 3203.24 |  |  | 193
1991-06-16 | 3203.45 |  |  | 193
1991-06-15 | 3203.66 |  |  | 193
1991-06-14 | 3203.85 |  |  | 193
1991-06-13 | 3204.05 |  |  | 193
1991-06-12 | 3204.24 |  |  | 193
1991-06-11 | 3204.42 |  |  | 193
1991-06-10 | 3204.62 |  |  | 193
1991-06-09 | 3204.73 |  |  | 193
1991-06-08 | 3204.84 |  |  | 193
1991-06-07 | 3204.95 |  |  | 193
1991-06-06 | 3205.1 |  |  | 193
1991-06-05 | 3205.23 |  |  | 193
1991-06-04 | 3205.38 |  |  | 193
1991-06-03 | 3205.54 |  |  | 193
1991-06-02 | 3205.67 |  |  | 193
1991-06-01 | 3205.77 |  |  | 193
1991-05-31 | 3205.81 |  |  | 196
1991-05-30 | 3205.9 |  |  | 200
1991-05-29 | 3205.98 |  |  | 200
1991-05-28 | 3205.98 |  |  | 191
1991-05-27 | 3205.98 |  |  | 168
1991-05-26 | 3205.96 |  |  | 154
1991-05-25 | 3205.94 |  |  | 154
1991-05-24 | 3205.92 |  |  | 132
1991-05-23 | 3205.79 |  |  | 100
1991-05-22 | 3205.59 |  |  | 100
1991-05-21 | 3205.22 |  |  | 100
1991-05-20 | 3204.75 |  |  | 100
1991-05-19 | 3204.35 |  |  | 100
1991-05-18 | 3203.97 |  |  | 99
1991-05-17 | 3203.63 |  |  | 154
1991-05-16 | 3203.54 |  |  | 198
1991-05-15 | 3203.52 |  |  | 198
1991-05-14 | 3203.52 |  |  | 198
1991-05-13 | 3203.49 |  |  | 198
1991-05-12 | 3203.49 |  |  | 198
1991-05-11 | 3203.49 |  |  | 198
1991-05-10 | 3203.49 |  |  | 198
1991-05-09 | 3203.47 |  |  | 198
1991-05-08 | 3203.47 |  |  | 198
1991-05-07 | 3203.5 |  |  | 198
1991-05-06 | 3203.53 |  |  | 198
1991-05-05 | 3203.6 |  |  | 198
1991-05-04 | 3203.66 |  |  | 198
1991-05-03 | 3203.69 |  |  | 198
1991-05-02 | 3203.76 |  |  | 198
1991-05-01 | 3203.79 |  |  | 189
1991-04-30 | 3203.79 |  |  | 164
1991-04-29 | 3203.73 |  |  | 152
1991-04-28 | 3203.7 |  |  | 152
1991-04-27 | 3203.63 |  |  | 152
1991-04-26 | 3203.55 |  |  | 152
1991-04-25 | 3203.43 |  |  | 152
1991-04-24 | 3203.24 |  |  | 152
1991-04-23 | 3203.07 |  |  | 141
1991-04-22 | 3202.8 |  |  | 134
1991-04-21 | 3202.59 |  |  | 132
1991-04-20 | 3202.47 |  |  | 130
1991-04-19 | 3202.38 |  |  | 120
1991-04-18 | 3202.22 |  |  | 107
1991-04-17 | 3202.14 |  |  | 105
1991-04-16 | 3202.04 |  |  | 103
1991-04-15 | 3202.02 |  |  | 86
1991-04-14 | 3201.94 |  |  | 40
1991-04-13 | 3201.69 |  |  | 30
1991-04-12 | 3201.54 |  |  | 30
1991-04-11 | 3201.39 |  |  | 30
1991-04-10 | 3199.28 |  |  | 30
1991-04-09 | 3199.28 |  |  | 30
1991-04-08 | 3199.28 |  |  | 30
1991-04-07 | 3199.28 |  |  | 30
1991-04-06 | 3199.28 |  |  | 30
1991-04-05 | 3199.28 |  |  | 30
1991-04-04 | 3199.12 |  |  | 30
1991-04-03 | 3198.88 |  |  | 30
1991-04-02 | 3198.6 |  |  | 30
1991-04-01 | 3198.37 |  |  | 30
1991-03-31 | 3198.2 |  |  | 30
1991-03-30 | 3198.02 |  |  | 30
1991-03-29 | 3197.86 |  |  | 29
1991-03-28 | 3197.71 |  |  | 29
1991-03-27 | 3197.48 |  |  | 29
1991-03-26 | 3197.27 |  |  | 29
1991-03-25 | 3197.01 |  |  | 30
1991-03-24 | 3196.8 |  |  | 30
1991-03-23 | 3196.66 |  |  | 30
1991-03-22 | 3196.47 |  |  | 30
1991-03-21 | 3196.28 |  |  | 30
1991-03-20 | 3196.07 |  |  | 30
1991-03-19 | 3195.94 |  |  | 30
1991-03-18 | 3195.8 |  |  | 30
1991-03-17 | 3195.61 |  |  | 30
1991-03-16 | 3195.48 |  |  | 30
1991-03-15 | 3195.37 |  |  | 30
1991-03-14 | 3195.24 |  |  | 30
1991-03-13 | 3195.16 |  |  | 30
1991-03-12 | 3194.99 |  |  | 30
1991-03-11 | 3194.85 |  |  | 30
1991-03-10 | 3194.72 |  |  | 30
1991-03-09 | 3194.57 |  |  | 30
1991-03-08 | 3194.42 |  |  | 30
1991-03-07 | 3194.26 |  |  | 30
1991-03-06 | 3194.06 |  |  | 30
1991-03-05 | 3193.81 |  |  | 30
1991-03-04 | 3193.47 |  |  | 30
1991-03-03 | 3193.34 |  |  | 30
1991-03-02 | 3193.14 |  |  | 30
1991-03-01 | 3192.95 |  |  | 30
1991-02-28 | 3192.9 |  |  | 31
1991-02-27 | 3192.73 |  |  | 31
1991-02-26 | 3192.6 |  |  | 31
1991-02-25 | 3192.48 |  |  | 30
1991-02-24 | 3192.42 |  |  | 30
1991-02-23 | 3192.3 |  |  | 30
1991-02-22 | 3192.23 |  |  | 30
1991-02-21 | 3192.09 |  |  | 30
1991-02-20 | 3191.97 |  |  | 30
1991-02-19 | 3191.86 |  |  | 30
1991-02-18 | 3191.68 |  |  | 30
1991-02-17 | 3191.49 |  |  | 30
1991-02-16 | 3191.25 |  |  | 30
1991-02-15 | 3190.93 |  |  | 30
1991-02-14 | 3190.53 |  |  | 30
1991-02-13 | 3190.33 |  |  | 30
1991-02-12 | 3190.07 |  |  | 30
1991-02-11 | 3190.01 |  |  | 30
1991-02-10 | 3189.82 |  |  | 30
1991-02-09 | 3189.66 |  |  | 30
1991-02-08 | 3189.53 |  |  | 30
1991-02-07 | 3189.39 |  |  | 30
1991-02-06 | 3189.24 |  |  | 36
1991-02-05 | 3188.95 |  |  | 43
1991-02-04 | 3188.69 |  |  | 46
1991-02-03 | 3188.62 |  |  | 46
1991-02-02 | 3188.53 |  |  | 47
1991-02-01 | 3188.5 |  |  | 48
1991-01-31 | 3188.44 |  |  | 49
1991-01-30 | 3188.4 |  |  | 49
1991-01-29 | 3188.37 |  |  | 49
1991-01-28 | 3188.32 |  |  | 49
1991-01-27 | 3188.3 |  |  | 49
1991-01-26 | 3188.28 |  |  | 49
1991-01-25 | 3188.25 |  |  | 49
1991-01-24 | 3188.16 |  |  | 49
1991-01-23 | 3188.08 |  |  | 49
1991-01-22 | 3188.04 |  |  | 49
1991-01-21 | 3187.99 |  |  | 49
1991-01-20 | 3187.94 |  |  | 49
1991-01-19 | 3187.85 |  |  | 50
1991-01-18 | 3187.76 |  |  | 52
1991-01-17 | 3187.56 |  |  | 60
1991-01-16 | 3187.24 |  |  | 71
1991-01-15 | 3186.83 |  |  | 74
1991-01-14 | 3186.49 |  |  | 77
1991-01-13 | 3186.47 |  |  | 77
1991-01-12 | 3186.46 |  |  | 77
1991-01-11 | 3186.46 |  |  | 77
1991-01-10 | 3186.5 |  |  | 77
1991-01-09 | 3186.5 |  |  | 77
1991-01-08 | 3186.51 |  |  | 77
1991-01-07 | 3186.53 |  |  | 77
1991-01-06 | 3186.54 |  |  | 77
1991-01-05 | 3186.55 |  |  | 77
1991-01-04 | 3186.55 |  |  | 77
1991-01-03 | 3186.66 |  |  | 77
1991-01-02 | 3186.66 |  |  | 77
1991-01-01 | 3186.67 |  |  | 77
1990-12-31 | 3186.68 |  |  | 77
1990-12-30 | 3186.73 |  |  | 77
1990-12-29 | 3186.77 |  |  | 77
1990-12-28 | 3186.83 |  |  | 77
1990-12-27 | 3186.83 |  |  | 77
1990-12-26 | 3186.85 |  |  | 77
1990-12-25 | 3186.92 |  |  | 77
1990-12-24 | 3186.98 |  |  | 77
1990-12-23 | 3187.08 |  |  | 77
1990-12-22 | 3187.13 |  |  | 77
1990-12-21 | 3187.21 |  |  | 77
1990-12-20 | 3187.28 |  |  | 77
1990-12-19 | 3187.38 |  |  | 77
1990-12-18 | 3187.38 |  |  | 77
1990-12-17 | 3187.38 |  |  | 77
1990-12-16 | 3187.38 |  |  | 71
1990-12-15 | 3187.44 |  |  | 78
1990-12-14 | 3187.47 |  |  | 78
1990-12-13 | 3187.48 |  |  | 78
1990-12-12 | 3187.48 |  |  | 78
1990-12-11 | 3187.49 |  |  | 78
1990-12-10 | 3187.49 |  |  | 78
1990-12-09 | 3187.49 |  |  | 78
1990-12-08 | 3187.5 |  |  | 77
1990-12-07 | 3187.51 |  |  | 77
1990-12-06 | 3187.56 |  |  | 77
1990-12-05 | 3187.56 |  |  | 77
1990-12-04 | 3187.56 |  |  | 77
1990-12-03 | 3187.63 |  |  | 77
1990-12-02 | 3187.65 |  |  | 77
1990-12-01 | 3187.65 |  |  | 77
1990-11-30 | 3187.67 |  |  | 77
1990-11-29 | 3187.69 |  |  | 77
1990-11-28 | 3187.7 |  |  | 77
1990-11-27 | 3187.7 |  |  | 77
1990-11-26 | 3187.71 |  |  | 77
1990-11-25 | 3187.72 |  |  | 77
1990-11-24 | 3187.72 |  |  | 77
1990-11-23 | 3187.72 |  |  | 77
1990-11-22 | 3187.81 |  |  | 77
1990-11-21 | 3187.81 |  |  | 77
1990-11-20 | 3187.82 |  |  | 77
1990-11-19 | 3187.82 |  |  | 77
1990-11-18 | 3187.84 |  |  | 77
1990-11-17 | 3187.94 |  |  | 77
1990-11-16 | 3188.04 |  |  | 77
1990-11-15 | 3188.14 |  |  | 77
1990-11-14 | 3187.94 |  |  | 77
1990-11-13 | 3187.95 |  |  | 77
1990-11-12 | 3187.95 |  |  | 77
1990-11-11 | 3187.99 |  |  | 77
1990-11-10 | 3187.99 |  |  | 77
1990-11-09 | 3187.99 |  |  | 77
1990-11-08 | 3188.05 |  |  | 77
1990-11-07 | 3188.05 |  |  | 77
1990-11-06 | 3188.06 |  |  | 77
1990-11-05 | 3188.06 |  |  | 77
1990-11-04 | 3188.06 |  |  | 77
1990-11-03 | 3188.12 |  |  | 77
1990-11-02 | 3188.15 |  |  | 77
1990-11-01 | 3188.17 |  |  | 77
1990-10-31 | 3188.17 |  |  | 77
1990-10-30 | 3188.23 |  |  | 77
1990-10-29 | 3188.25 |  |  | 77
1990-10-28 | 3188.3 |  |  | 77
1990-10-27 | 3188.33 |  |  | 77
1990-10-26 | 3188.38 |  |  | 77
1990-10-25 | 3188.42 |  |  | 77
1990-10-24 | 3188.45 |  |  | 77
1990-10-23 | 3188.47 |  |  | 77
1990-10-22 | 3188.55 |  |  | 77
1990-10-21 | 3188.56 |  |  | 77
1990-10-20 | 3188.57 |  |  | 77
1990-10-19 | 3188.58 |  |  | 71
1990-10-18 | 3188.64 |  |  | 62
1990-10-17 | 3188.64 |  |  | 62
1990-10-16 | 3188.64 |  |  | 91
1990-10-15 | 3188.78 |  |  | 136
1990-10-14 | 3188.93 |  |  | 137
1990-10-13 | 3189.08 |  |  | 136
1990-10-12 | 3189.25 |  |  | 150
1990-10-11 | 3189.42 |  |  | 164
1990-10-10 | 3189.61 |  |  | 164
1990-10-09 | 3189.84 |  |  | 164
1990-10-08 | 3199.81 |  |  | 164
1990-10-07 | 3199.81 |  |  | 164
1990-10-06 | 3199.81 |  |  | 165
1990-10-05 | 3199.81 |  |  | 177
1990-10-04 | 3199.81 |  |  | 190
1990-10-03 | 3199.81 |  |  | 191
1990-10-02 | 3199.81 |  |  | 195
1990-10-01 | 3199.81 |  |  | 198
1990-09-30 | 3199.81 |  |  | 201
1990-09-29 | 3199.81 |  |  | 203
1990-09-28 | 3199.81 |  |  | 215
1990-09-27 | 3199.82 |  |  | 232
1990-09-26 | 3199.82 |  |  | 232
1990-09-25 | 3199.82 |  |  | 232
1990-09-24 | 3199.82 |  |  | 232
1990-09-23 | 3199.82 |  |  | 232
1990-09-22 | 3199.82 |  |  | 232
1990-09-21 | 3199.82 |  |  | 234
1990-09-20 | 3199.82 |  |  | 234
1990-09-19 | 3199.82 |  |  | 234
1990-09-18 | 3199.82 |  |  | 234
1990-09-17 | 3199.82 |  |  | 235
1990-09-16 | 3199.82 |  |  | 236
1990-09-15 | 3199.82 |  |  | 236
1990-09-14 | 3199.82 |  |  | 236
1990-09-13 | 3199.84 |  |  | 236
1990-09-12 | 3199.84 |  |  | 236
1990-09-11 | 3199.84 |  |  | 236
1990-09-10 | 3199.84 |  |  | 236
1990-09-09 | 3199.84 |  |  | 236
1990-09-08 | 3199.84 |  |  | 236
1990-09-07 | 3199.84 |  |  | 236
1990-09-06 | 3199.84 |  |  | 236
1990-09-05 | 3199.85 |  |  | 236
1990-09-04 | 3199.85 |  |  | 236
1990-09-03 | 3199.86 |  |  | 236
1990-09-02 | 3199.94 |  |  | 236
1990-09-01 | 3200.08 |  |  | 236
1990-08-31 | 3200.21 |  |  | 236
1990-08-30 | 3200.38 |  |  | 236
1990-08-29 | 3200.66 |  |  | 236
1990-08-28 | 3200.94 |  |  | 236
1990-08-27 | 3201.2 |  |  | 236
1990-08-26 | 3201.46 |  |  | 236
1990-08-25 | 3201.72 |  |  | 236
1990-08-24 | 3202 |  |  | 236
1990-08-23 | 3202.29 |  |  | 237
1990-08-22 | 3202.57 |  |  | 238
1990-08-21 | 3202.82 |  |  | 238
1990-08-20 | 3203.07 |  |  | 238
1990-08-19 | 3203.31 |  |  | 238
1990-08-18 | 3203.58 |  |  | 239
1990-08-17 | 3203.83 |  |  | 239
1990-08-16 | 3204.11 |  |  | 238
1990-08-15 | 3204.38 |  |  | 240
1990-08-14 | 3204.69 |  |  | 240
1990-08-13 | 3204.97 |  |  | 240
1990-08-12 | 3205.25 |  |  | 240
1990-08-11 | 3205.51 |  |  | 240
1990-08-10 | 3205.76 |  |  | 240
1990-08-09 | 3206.02 |  |  | 240
1990-08-08 | 3206.29 |  |  | 240
1990-08-07 | 3206.56 |  |  | 241
1990-08-06 | 3206.82 |  |  | 241
1990-08-05 | 3207.09 |  |  | 241
1990-08-04 | 3207.34 |  |  | 243
1990-08-03 | 3207.6 |  |  | 243
1990-08-02 | 3207.85 |  |  | 243
1990-08-01 | 3208.11 |  |  | 243
1990-07-31 | 3208.39 |  |  | 232
1990-07-30 | 3208.66 |  |  | 221
1990-07-29 | 3208.91 |  |  | 221
1990-07-28 | 3209.12 |  |  | 222
1990-07-27 | 3209.33 |  |  | 222
1990-07-26 | 3209.58 |  |  | 222
1990-07-25 | 3209.79 |  |  | 222
1990-07-24 | 3210.03 |  |  | 222
1990-07-23 | 3210.29 |  |  | 222
1990-07-22 | 3210.58 |  |  | 222
1990-07-21 | 3210.8 |  |  | 222
1990-07-20 | 3211 |  |  | 222
1990-07-19 | 3211.24 |  |  | 222
1990-07-18 | 3211.46 |  |  | 222
1990-07-17 | 3211.69 |  |  | 222
1990-07-16 | 3211.91 |  |  | 222
1990-07-15 | 3212.16 |  |  | 222
1990-07-14 | 3212.38 |  |  | 222
1990-07-13 | 3212.6 |  |  | 222
1990-07-12 | 3212.8 |  |  | 222
1990-07-11 | 3212.97 |  |  | 223
1990-07-10 | 3213.19 |  |  | 222
1990-07-09 | 3213.39 |  |  | 222
1990-07-08 | 3213.61 |  |  | 222
1990-07-07 | 3213.79 |  |  | 222
1990-07-06 | 3213.99 |  |  | 224
1990-07-05 | 3214.19 |  |  | 223
1990-07-04 | 3214.4 |  |  | 223
1990-07-03 | 3214.6 |  |  | 224
1990-07-02 | 3214.83 |  |  | 224
1990-07-01 | 3215.03 |  |  | 224
1990-06-30 | 3215.25 |  |  | 224
1990-06-29 | 3215.48 |  |  | 224
1990-06-28 | 3215.67 |  |  | 224
1990-06-27 | 3215.87 |  |  | 224
1990-06-26 | 3216.12 |  |  | 224
1990-06-25 | 3216.33 |  |  | 224
1990-06-24 | 3216.54 |  |  | 224
1990-06-23 | 3216.68 |  |  | 224
1990-06-22 | 3216.86 |  |  | 224
1990-06-21 | 3217.05 |  |  | 224
1990-06-20 | 3217.23 |  |  | 224
1990-06-19 | 3217.45 |  |  | 224
1990-06-18 | 3217.58 |  |  | 224
1990-06-17 | 3217.75 |  |  | 224
1990-06-16 | 3217.93 |  |  | 224
1990-06-15 | 3218.07 |  |  | 224
1990-06-14 | 3218.25 |  |  | 224
1990-06-13 | 3218.41 |  |  | 224
1990-06-12 | 3218.59 |  |  | 225
1990-06-11 | 3218.75 |  |  | 224
1990-06-10 | 3218.9 |  |  | 224
1990-06-09 | 3219.05 |  |  | 224
1990-06-08 | 3219.19 |  |  | 214
1990-06-07 | 3219.29 |  |  | 199
1990-06-06 | 3219.37 |  |  | 199
1990-06-05 | 3219.4 |  |  | 199
1990-06-04 | 3219.54 |  |  | 200
1990-06-03 | 3219.61 |  |  | 200
1990-06-02 | 3219.69 |  |  | 200
1990-06-01 | 3219.73 |  |  | 200
1990-05-31 | 3219.74 |  |  | 225
1990-05-30 | 3219.82 |  |  | 253
1990-05-29 | 3219.87 |  |  | 253
1990-05-28 | 3219.93 |  |  | 253
1990-05-27 | 3220.09 |  |  | 253
1990-05-26 | 3220.23 |  |  | 253
1990-05-25 | 3220.4 |  |  | 253
1990-05-24 | 3220.52 |  |  | 253
1990-05-23 | 3220.73 |  |  | 253
1990-05-22 | 3220.88 |  |  | 253
1990-05-21 | 3221.08 |  |  | 253
1990-05-20 | 3221.27 |  |  | 253
1990-05-19 | 3221.47 |  |  | 253
1990-05-18 | 3221.67 |  |  | 253
1990-05-17 | 3221.89 |  |  | 253
1990-05-16 | 3222.1 |  |  | 253
1990-05-15 | 3222.29 |  |  | 253
1990-05-14 | 3222.49 |  |  | 253
1990-05-13 | 3222.69 |  |  | 253
1990-05-12 | 3222.87 |  |  | 253
1990-05-11 | 3223.07 |  |  | 253
1990-05-10 | 3223.27 |  |  | 253
1990-05-09 | 3223.42 |  |  | 253
1990-05-08 | 3223.64 |  |  | 238
1990-05-07 | 3223.75 |  |  | 216
1990-05-06 | 3223.93 |  |  | 216
1990-05-05 | 3224.13 |  |  | 216
1990-05-04 | 3224.23 |  |  | 216
1990-05-03 | 3224.31 |  |  | 216
1990-05-02 | 3224.39 |  |  | 216
1990-05-01 | 3224.45 |  |  | 216
1990-04-30 | 3224.5 |  |  | 216
1990-04-29 | 3224.51 |  |  | 216
1990-04-28 | 3224.5 |  |  | 216
1990-04-27 | 3224.62 |  |  | 216
1990-04-26 | 3224.74 |  |  | 216
1990-04-25 | 3224.85 |  |  | 216
1990-04-24 | 3225.02 |  |  | 216
1990-04-23 | 3225.15 |  |  | 216
1990-04-22 | 3225.24 |  |  | 216
1990-04-21 | 3225.35 |  |  | 216
1990-04-20 | 3225.46 |  |  | 216
1990-04-19 | 3225.57 |  |  | 216
1990-04-18 | 3225.69 |  |  | 216
1990-04-17 | 3225.8 |  |  | 216
1990-04-16 | 3225.8 |  |  | 124
1990-04-15 | 3225.74 |  |  | 76
1990-04-14 | 3225.68 |  |  | 76
1990-04-13 | 3225.66 |  |  | 76
1990-04-12 | 3225.58 |  |  | 76
1990-04-11 | 3225.53 |  |  | 76
1990-04-10 | 3225.48 |  |  | 76
1990-04-09 | 3225.38 |  |  | 76
1990-04-08 | 3225.26 |  |  | 76
1990-04-07 | 3225.17 |  |  | 75
1990-04-06 | 3224.99 |  |  | 75
1990-04-05 | 3224.79 |  |  | 75
1990-04-04 | 3224.6 |  |  | 75
1990-04-03 | 3224.35 |  |  | 75
1990-04-02 | 3224.08 |  |  | 75
1990-04-01 | 3223.73 |  |  | 75
1990-03-31 | 3223.43 |  |  | 75
1990-03-30 | 3223.21 |  |  | 75
1990-03-29 | 3222.96 |  |  | 75
1990-03-28 | 3222.73 |  |  | 75
1990-03-27 | 3222.49 |  |  | 75
1990-03-26 | 3222.22 |  |  | 75
1990-03-25 | 3221.92 |  |  | 75
1990-03-24 | 3221.54 |  |  | 75
1990-03-23 | 3221.17 |  |  | 75
1990-03-22 | 3220.67 |  |  | 74
1990-03-21 | 3220.19 |  |  | 74
1990-03-20 | 3219.77 |  |  | 74
1990-03-19 | 3219.3 |  |  | 74
1990-03-18 | 3218.77 |  |  | 74
1990-03-17 | 3218.44 |  |  | 74
1990-03-16 | 3218.31 |  |  | 74
1990-03-15 | 3218.17 |  |  | 74
1990-03-14 | 3218.05 |  |  | 74
1990-03-13 | 3217.89 |  |  | 74
1990-03-12 | 3217.78 |  |  | 74
1990-03-11 | 3217.49 |  |  | 74
1990-03-10 | 3217.12 |  |  | 74
1990-03-09 | 3216.98 |  |  | 74
1990-03-08 | 3216.81 |  |  | 74
1990-03-07 | 3216.69 |  |  | 74
1990-03-06 | 3216.53 |  |  | 74
1990-03-05 | 3216.32 |  |  | 74
1990-03-04 | 3216.01 |  |  | 74
1990-03-03 | 3215.77 |  |  | 74
1990-03-02 | 3215.54 |  |  | 74
1990-03-01 | 3215.44 |  |  | 74
1990-02-28 | 3215.34 |  |  | 74
1990-02-27 | 3215.18 |  |  | 74
1990-02-26 | 3215.02 |  |  | 74
1990-02-25 | 3214.92 |  |  | 74
1990-02-24 | 3214.85 |  |  | 74
1990-02-23 | 3214.8 |  |  | 74
1990-02-22 | 3214.7 |  |  | 75
1990-02-21 | 3214.69 |  |  | 75
1990-02-20 | 3214.68 |  |  | 75
1990-02-19 | 3214.68 |  |  | 75
1990-02-18 | 3214.68 |  |  | 75
1990-02-17 | 3214.68 |  |  | 75
1990-02-16 | 3214.68 |  |  | 75
1990-02-15 | 3214.65 |  |  | 75
1990-02-14 | 3214.65 |  |  | 75
1990-02-13 | 3214.65 |  |  | 75
1990-02-12 | 3214.65 |  |  | 68
1990-02-11 | 3214.58 |  |  | 58
1990-02-10 | 3214.57 |  |  | 58
1990-02-09 | 3214.57 |  |  | 59
1990-02-08 | 3214.47 |  |  | 58
1990-02-07 | 3214.47 |  |  | 58
1990-02-06 | 3214.4 |  |  | 58
1990-02-05 | 3214.38 |  |  | 58
1990-02-04 | 3214.36 |  |  | 58
1990-02-03 | 3214.31 |  |  | 58
1990-02-02 | 3214.26 |  |  | 58
1990-02-01 | 3214.23 |  |  | 58
1990-01-31 | 3214.23 |  |  | 58
1990-01-30 | 3214.16 |  |  | 58
1990-01-29 | 3214.13 |  |  | 58
1990-01-28 | 3214.1 |  |  | 58
1990-01-27 | 3214.08 |  |  | 58
1990-01-26 | 3214.08 |  |  | 58
1990-01-25 | 3213.99 |  |  | 57
1990-01-24 | 3213.98 |  |  | 57
1990-01-23 | 3213.95 |  |  | 57
1990-01-22 | 3213.93 |  |  | 57
1990-01-21 | 3213.84 |  |  | 57
1990-01-20 | 3213.78 |  |  | 57
1990-01-19 | 3213.76 |  |  | 57
1990-01-18 | 3213.75 |  |  | 57
1990-01-17 | 3213.68 |  |  | 57
1990-01-16 | 3213.62 |  |  | 57
1990-01-15 | 3213.53 |  |  | 57
1990-01-14 | 3213.38 |  |  | 57
1990-01-13 | 3213.24 |  |  | 57
1990-01-12 | 3213.11 |  |  | 57
1990-01-11 | 3212.97 |  |  | 57
1990-01-10 | 3212.77 |  |  | 57
1990-01-09 | 3212.63 |  |  | 57
1990-01-08 | 3212.33 |  |  | 57
1990-01-07 | 3212.2 |  |  | 57
1990-01-06 | 3212.12 |  |  | 57
1990-01-05 | 3212.09 |  |  | 57
1990-01-04 | 3212.02 |  |  | 57
1990-01-03 | 3212.02 |  |  | 57
1990-01-02 | 3212.01 |  |  | 57
1990-01-01 | 3212.01 |  |  | 57
1989-12-31 | 3212 |  |  | 57
1989-12-30 | 3211.95 |  |  | 57
1989-12-29 | 3211.94 |  |  | 57
1989-12-28 | 3211.94 |  |  | 57
1989-12-27 | 3211.94 |  |  | 57
1989-12-26 | 3211.93 |  |  | 57
1989-12-25 | 3211.93 |  |  | 56
1989-12-24 | 3211.91 |  |  | 56
1989-12-23 | 3211.88 |  |  | 56
1989-12-22 | 3211.87 |  |  | 56
1989-12-21 | 3211.83 |  |  | 56
1989-12-20 | 3211.82 |  |  | 56
1989-12-19 | 3211.8 |  |  | 56
1989-12-18 | 3211.79 |  |  | 56
1989-12-17 | 3211.78 |  |  | 56
1989-12-16 | 3211.78 |  |  | 56
1989-12-15 | 3211.77 |  |  | 56
1989-12-14 | 3211.75 |  |  | 56
1989-12-13 | 3211.74 |  |  | 56
1989-12-12 | 3211.66 |  |  | 56
1989-12-11 | 3211.66 |  |  | 56
1989-12-10 | 3211.63 |  |  | 56
1989-12-09 | 3211.62 |  |  | 56
1989-12-08 | 3211.61 |  |  | 46
1989-12-07 | 3211.47 |  |  | 31
1989-12-06 | 3211.44 |  |  | 49
1989-12-05 | 3211.33 |  |  | 59
1989-12-04 | 3211.3 |  |  | 59
1989-12-03 | 3211.26 |  |  | 58
1989-12-02 | 3211.26 |  |  | 58
1989-12-01 | 3211.25 |  |  | 58
1989-11-30 | 3211.25 |  |  | 58
1989-11-29 | 3211.17 |  |  | 58
1989-11-28 | 3211.17 |  |  | 58
1989-11-27 | 3211.16 |  |  | 58
1989-11-26 | 3211.16 |  |  | 58
1989-11-25 | 3211.15 |  |  | 58
1989-11-24 | 3211.15 |  |  | 58
1989-11-23 | 3211.06 |  |  | 58
1989-11-22 | 3211.05 |  |  | 57
1989-11-21 | 3211.04 |  |  | 57
1989-11-20 | 3211.04 |  |  | 57
1989-11-19 | 3211.04 |  |  | 57
1989-11-18 | 3211.03 |  |  | 57
1989-11-17 | 3211.03 |  |  | 53
1989-11-16 | 3211 |  |  | 57
1989-11-15 | 3211 |  |  | 57
1989-11-14 | 3211 |  |  | 58
1989-11-13 | 3211 |  |  | 72
1989-11-12 | 3211.02 |  |  | 91
1989-11-11 | 3211.02 |  |  | 91
1989-11-10 | 3211.02 |  |  | 78
1989-11-09 | 3211.02 |  |  | 58
1989-11-08 | 3210.89 |  |  | 58
1989-11-07 | 3210.89 |  |  | 58
1989-11-06 | 3210.88 |  |  | 58
1989-11-05 | 3210.88 |  |  | 58
1989-11-04 | 3210.88 |  |  | 58
1989-11-03 | 3210.87 |  |  | 64
1989-11-02 | 3210.88 |  |  | 71
1989-11-01 | 3210.88 |  |  | 71
1989-10-31 | 3210.88 |  |  | 71
1989-10-30 | 3210.89 |  |  | 71
1989-10-29 | 3210.89 |  |  | 71
1989-10-28 | 3210.89 |  |  | 71
1989-10-27 | 3210.89 |  |  | 71
1989-10-26 | 3210.92 |  |  | 71
1989-10-25 | 3210.92 |  |  | 71
1989-10-24 | 3210.92 |  |  | 71
1989-10-23 | 3210.92 |  |  | 71
1989-10-22 | 3210.93 |  |  | 71
1989-10-21 | 3210.96 |  |  | 71
1989-10-20 | 3210.97 |  |  | 71
1989-10-19 | 3211.02 |  |  | 71
1989-10-18 | 3211.03 |  |  | 71
1989-10-17 | 3211.03 |  |  | 71
1989-10-16 | 3211.06 |  |  | 71
1989-10-15 | 3211.09 |  |  | 71
1989-10-14 | 3211.11 |  |  | 71
1989-10-13 | 3211.12 |  |  | 82
1989-10-12 | 3211.22 |  |  | 99
1989-10-11 | 3211.27 |  |  | 99
1989-10-10 | 3211.31 |  |  | 99
1989-10-09 | 3211.39 |  |  | 99
1989-10-08 | 3211.44 |  |  | 98
1989-10-07 | 3211.48 |  |  | 98
1989-10-06 | 3211.55 |  |  | 108
1989-10-05 | 3211.62 |  |  | 124
1989-10-04 | 3211.7 |  |  | 124
1989-10-03 | 3211.78 |  |  | 124
1989-10-02 | 3211.86 |  |  | 124
1989-10-01 | 3211.95 |  |  | 124
1989-09-30 | 3212.05 |  |  | 154
1989-09-29 | 3212.19 |  |  | 173
1989-09-28 | 3212.29 |  |  | 173
1989-09-27 | 3212.42 |  |  | 173
1989-09-26 | 3212.54 |  |  | 173
1989-09-25 | 3212.69 |  |  | 173
1989-09-24 | 3212.82 |  |  | 173
1989-09-23 | 3212.94 |  |  | 173
1989-09-22 | 3213.09 |  |  | 181
1989-09-21 | 3213.21 |  |  | 197
1989-09-20 | 3213.37 |  |  | 197
1989-09-19 | 3213.53 |  |  | 197
1989-09-18 | 3213.66 |  |  | 197
1989-09-17 | 3213.85 |  |  | 197
1989-09-16 | 3214.03 |  |  | 197
1989-09-15 | 3214.17 |  |  | 196
1989-09-14 | 3214.36 |  |  | 196
1989-09-13 | 3214.52 |  |  | 196
1989-09-12 | 3214.67 |  |  | 196
1989-09-11 | 3214.85 |  |  | 196
1989-09-10 | 3215.03 |  |  | 195
1989-09-09 | 3215.21 |  |  | 196
1989-09-08 | 3215.42 |  |  | 202
1989-09-07 | 3215.56 |  |  | 211
1989-09-06 | 3215.74 |  |  | 211
1989-09-05 | 3215.94 |  |  | 211
1989-09-04 | 3216.13 |  |  | 211
1989-09-03 | 3216.3 |  |  | 211
1989-09-02 | 3216.53 |  |  | 211
1989-09-01 | 3216.66 |  |  | 211
1989-08-31 | 3216.84 |  |  | 211
1989-08-30 | 3217 |  |  | 211
1989-08-29 | 3217.14 |  |  | 226
1989-08-28 | 3217.38 |  |  | 254
1989-08-27 | 3217.58 |  |  | 256
1989-08-26 | 3217.8 |  |  | 256
1989-08-25 | 3218.04 |  |  | 256
1989-08-24 | 3218.25 |  |  | 256
1989-08-23 | 3218.48 |  |  | 256
1989-08-22 | 3218.7 |  |  | 257
1989-08-21 | 3218.93 |  |  | 258
1989-08-20 | 3219.16 |  |  | 258
1989-08-19 | 3219.37 |  |  | 258
1989-08-18 | 3219.59 |  |  | 258
1989-08-17 | 3219.8 |  |  | 258
1989-08-16 | 3220.02 |  |  | 258
1989-08-15 | 3220.26 |  |  | 259
1989-08-14 | 3220.47 |  |  | 259
1989-08-13 | 3220.72 |  |  | 259
1989-08-12 | 3220.93 |  |  | 260
1989-08-11 | 3221.18 |  |  | 261
1989-08-10 | 3221.4 |  |  | 261
1989-08-09 | 3221.61 |  |  | 261
1989-08-08 | 3221.82 |  |  | 261
1989-08-07 | 3222.07 |  |  | 261
1989-08-06 | 3222.25 |  |  | 261
1989-08-05 | 3222.44 |  |  | 261
1989-08-04 | 3222.63 |  |  | 261
1989-08-03 | 3222.84 |  |  | 261
1989-08-02 | 3223.05 |  |  | 263
1989-08-01 | 3223.27 |  |  | 263
1989-07-31 | 3223.47 |  |  | 263
1989-07-30 | 3223.75 |  |  | 263
1989-07-29 | 3224.04 |  |  | 263
1989-07-28 | 3224.23 |  |  | 264
1989-07-27 | 3224.5 |  |  | 265
1989-07-26 | 3224.67 |  |  | 268
1989-07-25 | 3224.86 |  |  | 268
1989-07-24 | 3225.11 |  |  | 268
1989-07-23 | 3225.29 |  |  | 268
1989-07-22 | 3225.47 |  |  | 270
1989-07-21 | 3225.65 |  |  | 270
1989-07-20 | 3225.91 |  |  | 270
1989-07-19 | 3226.13 |  |  | 271
1989-07-18 | 3226.31 |  |  | 272
1989-07-17 | 3226.49 |  |  | 273
1989-07-16 | 3226.69 |  |  | 273
1989-07-15 | 3226.9 |  |  | 273
1989-07-14 | 3227.11 |  |  | 273
1989-07-13 | 3227.33 |  |  | 268
1989-07-12 | 3227.56 |  |  | 265
1989-07-11 | 3227.69 |  |  | 266
1989-07-10 | 3227.88 |  |  | 266
1989-07-09 | 3228.08 |  |  | 267
1989-07-08 | 3228.22 |  |  | 268
1989-07-07 | 3228.45 |  |  | 268
1989-07-06 | 3228.66 |  |  | 268
1989-07-05 | 3228.81 |  |  | 268
1989-07-04 | 3229 |  |  | 268
1989-07-03 | 3229.19 |  |  | 268
1989-07-02 | 3229.37 |  |  | 268
1989-07-01 | 3229.54 |  |  | 268
1989-06-30 | 3229.72 |  |  | 268
1989-06-29 | 3229.9 |  |  | 268
1989-06-28 | 3230.07 |  |  | 268
1989-06-27 | 3230.28 |  |  | 268
1989-06-26 | 3230.51 |  |  | 268
1989-06-25 | 3230.7 |  |  | 267
1989-06-24 | 3230.89 |  |  | 266
1989-06-23 | 3231.03 |  |  | 265
1989-06-22 | 3231.21 |  |  | 265
1989-06-21 | 3231.39 |  |  | 265
1989-06-20 | 3231.58 |  |  | 265
1989-06-19 | 3231.74 |  |  | 265
1989-06-18 | 3231.94 |  |  | 265
1989-06-17 | 3232.09 |  |  | 264
1989-06-16 | 3232.24 |  |  | 263
1989-06-15 | 3232.44 |  |  | 263
1989-06-14 | 3232.62 |  |  | 241
1989-06-13 | 3232.77 |  |  | 225
1989-06-12 | 3232.94 |  |  | 225
1989-06-11 | 3233.06 |  |  | 224
1989-06-10 | 3233.15 |  |  | 223
1989-06-09 | 3233.26 |  |  | 223
1989-06-08 | 3233.7 |  |  | 223
1989-06-07 | 3233.7 |  |  | 223
1989-06-06 | 3233.7 |  |  | 221
1989-06-05 | 3233.8 |  |  | 221
1989-06-04 | 3233.89 |  |  | 221
1989-06-03 | 3233.99 |  |  | 221
1989-06-02 | 3234.02 |  |  | 239
1989-06-01 | 3234.1 |  |  | 268
1989-05-31 | 3234.12 |  |  | 268
1989-05-30 | 3234.21 |  |  | 268
1989-05-29 | 3234.23 |  |  | 268
1989-05-28 | 3234.23 |  |  | 268
1989-05-27 | 3234.27 |  |  | 267
1989-05-26 | 3234.27 |  |  | 287
1989-05-25 | 3234.33 |  |  | 325
1989-05-24 | 3234.33 |  |  | 404
1989-05-23 | 3234.5 |  |  | 553
1989-05-22 | 3234.69 |  |  | 553
1989-05-21 | 3234.88 |  |  | 557
1989-05-20 | 3235.08 |  |  | 567
1989-05-19 | 3235.22 |  |  | 639
1989-05-18 | 3235.41 |  |  | 739
1989-05-17 | 3235.74 |  |  | 761
1989-05-16 | 3235.92 |  |  | 781
1989-05-15 | 3236.05 |  |  | 857
1989-05-14 | 3236.24 |  |  | 949
1989-05-13 | 3236.41 |  |  | 972
1989-05-12 | 3236.49 |  |  | 1040
1989-05-11 | 3236.47 |  |  | 1110
1989-05-10 | 3236.43 |  |  | 1100
1989-05-09 | 3236.59 |  |  | 1110
1989-05-08 | 3236.73 |  |  | 1120
1989-05-07 | 3236.78 |  |  | 1130
1989-05-06 | 3236.78 |  |  | 1130
1989-05-05 | 3236.78 |  |  | 1160
1989-05-04 | 3236.88 |  |  | 1250
1989-05-03 | 3236.95 |  |  | 1310
1989-05-02 | 3237.11 |  |  | 1440
1989-05-01 | 3237.2 |  |  | 1450
1989-04-30 | 3237.19 |  |  | 1310
1989-04-29 | 3236.92 |  |  | 1170
1989-04-28 | 3236.53 |  |  | 1110
1989-04-27 | 3236.12 |  |  | 1050
1989-04-26 | 3235.68 |  |  | 996
1989-04-25 | 3235.18 |  |  | 954
1989-04-24 | 3234.97 |  |  | 948
1989-04-23 | 3234.93 |  |  | 947
1989-04-22 | 3234.83 |  |  | 943
1989-04-21 | 3234.58 |  |  | 1030
1989-04-20 | 3234.38 |  |  | 1190
1989-04-19 | 3234.24 |  |  | 1180
1989-04-18 | 3234.03 |  |  | 1180
1989-04-17 | 3233.67 |  |  | 1290
1989-04-16 | 3233.43 |  |  | 1480
1989-04-15 | 3233.08 |  |  | 1480
1989-04-14 | 3232.79 |  |  | 1470
1989-04-13 | 3232.48 |  |  | 1570
1989-04-12 | 3232.33 |  |  | 1760
1989-04-11 | 3232.21 |  |  | 1760
1989-04-10 | 3232.13 |  |  | 1620
1989-04-09 | 3231.81 |  |  | 1380
1989-04-08 | 3231.08 |  |  | 1370
1989-04-07 | 3230.18 |  |  | 1470
1989-04-06 | 3229.72 |  |  | 1660
1989-04-05 | 3229.83 |  |  | 1660
1989-04-04 | 3230.23 |  |  | 1780
1989-04-03 | 3230.69 |  |  | 1980
1989-04-02 | 3231.18 |  |  | 1990
1989-04-01 | 3231.54 |  |  | 1980
1989-03-31 | 3231.89 |  |  | 1990
1989-03-30 | 3232.14 |  |  | 1990
1989-03-29 | 3232.26 |  |  | 1990
1989-03-28 | 3232.12 |  |  | 1990
1989-03-27 | 3232.12 |  |  | 1990
1989-03-26 | 3232.02 |  |  | 1990
1989-03-25 | 3231.44 |  |  | 1980
1989-03-24 | 3231.03 |  |  | 1980
1989-03-23 | 3231.03 |  |  | 1980
1989-03-22 | 3230.83 |  |  | 1980
1989-03-21 | 3230.6 |  |  | 2040
1989-03-20 | 3230.91 |  |  | 2260
1989-03-19 | 3231.48 |  |  | 2450
1989-03-18 | 3232.09 |  |  | 2460
1989-03-17 | 3232.79 |  |  | 2520
1989-03-16 | 3233.56 |  |  | 2660
1989-03-15 | 3234.19 |  |  | 2900
1989-03-14 | 3234.73 |  |  | 3010
1989-03-13 | 3234.91 |  |  | 3080
1989-03-12 | 3234.37 |  |  | 3070
1989-03-11 | 3233.37 |  |  | 3070
1989-03-10 | 3232.3 |  |  | 1870
1989-03-09 | 3229.99 |  |  | 728
1989-03-08 | 3228.5 |  |  | 401
1989-03-07 | 3227.52 |  |  | 324
1989-03-06 | 3225.54 |  |  | 199
1989-03-05 | 3224.42 |  |  | 199
1989-03-04 | 3224.2 |  |  | 199
1989-03-03 | 3224.02 |  |  | 199
1989-03-02 | 3223.81 |  |  | 199
1989-03-01 | 3223.42 |  |  | 199
1989-02-28 | 3223.18 |  |  | 199
1989-02-27 | 3222.91 |  |  | 199
1989-02-26 | 3222.51 |  |  | 199
1989-02-25 | 3221.99 |  |  | 139
1989-02-24 | 3221.19 |  |  | 47
1989-02-23 | 3219.79 |  |  | 19
1989-02-22 | 3217.67 |  |  | 19
1989-02-21 | 3216.86 |  |  | 19
1989-02-20 | 3216.15 |  |  | 19
1989-02-19 | 3215.13 |  |  | 19
1989-02-18 | 3214.16 |  |  | 19
1989-02-17 | 3213.96 |  |  | 19
1989-02-16 | 3213.86 |  |  | 19
1989-02-15 | 3213.74 |  |  | 19
1989-02-14 | 3213.67 |  |  | 19
1989-02-13 | 3213.61 |  |  | 19
1989-02-12 | 3213.52 |  |  | 19
1989-02-11 | 3213.44 |  |  | 19
1989-02-10 | 3213.38 |  |  | 19
1989-02-09 | 3213.32 |  |  | 19
1989-02-08 | 3213.24 |  |  | 19
1989-02-07 | 3213.16 |  |  | 19
1989-02-06 | 3213.08 |  |  | 19
1989-02-05 | 3212.99 |  |  | 19
1989-02-04 | 3212.91 |  |  | 19
1989-02-03 | 3212.9 |  |  | 19
1989-02-02 | 3212.84 |  |  | 19
1989-02-01 | 3212.75 |  |  | 19
1989-01-31 | 3212.64 |  |  | 19
1989-01-30 | 3212.52 |  |  | 19
1989-01-29 | 3212.42 |  |  | 19
1989-01-28 | 3212.3 |  |  | 19
1989-01-27 | 3212.2 |  |  | 19
1989-01-26 | 3212.09 |  |  | 19
1989-01-25 | 3211.98 |  |  | 19
1989-01-24 | 3211.91 |  |  | 19
1989-01-23 | 3211.85 |  |  | 19
1989-01-22 | 3211.74 |  |  | 19
1989-01-21 | 3211.61 |  |  | 19
1989-01-20 | 3211.47 |  |  | 19
1989-01-19 | 3211.32 |  |  | 19
1989-01-18 | 3211.2 |  |  | 19
1989-01-17 | 3211.05 |  |  | 19
1989-01-16 | 3210.94 |  |  | 19
1989-01-15 | 3210.81 |  |  | 19
1989-01-14 | 3210.69 |  |  | 19
1989-01-13 | 3210.55 |  |  | 19
1989-01-12 | 3210.46 |  |  | 19
1989-01-11 | 3210.32 |  |  | 19
1989-01-10 | 3210.14 |  |  | 19
1989-01-09 | 3210 |  |  | 19
1989-01-08 | 3209.81 |  |  | 19
1989-01-07 | 3209.75 |  |  | 19
1989-01-06 | 3209.71 |  |  | 12
1989-01-05 | 3209.57 |  |  | 7.9
1989-01-04 | 3209.46 |  |  | 7.8
1989-01-03 | 3209.34 |  |  | 7.6
1989-01-02 | 3209.22 |  |  | 7.6
1989-01-01 | 3209.01 |  |  | 7.6
1988-12-31 | 3208.92 |  |  | 7.6
1988-12-30 | 3208.92 |  |  | 7.6
1988-12-29 | 3208.81 |  |  | 7.6
1988-12-28 | 3208.76 |  |  | 7.6
1988-12-27 | 3208.69 |  |  | 7.6
1988-12-26 | 3208.64 |  |  | 7.6
1988-12-25 | 3208.56 |  |  | 7.6
1988-12-24 | 3208.49 |  |  | 7.6
1988-12-23 | 3208.4 |  |  | 7.6
1988-12-22 | 3208.25 |  |  | 7.6
1988-12-21 | 3208.2 |  |  | 7.5
1988-12-20 | 3208.05 |  |  | 7.5
1988-12-19 | 3207.96 |  |  | 7.4
1988-12-18 | 3207.83 |  |  | 7.4
1988-12-17 | 3207.76 |  |  | 7.5
1988-12-16 | 3207.68 |  |  | 7.4
1988-12-15 | 3207.59 |  |  | 7.3
1988-12-14 | 3207.45 |  |  | 7.2
1988-12-13 | 3207.24 |  |  | 7.1
1988-12-12 | 3207.01 |  |  | 12
1988-12-11 | 3206.7 |  |  | 19
1988-12-10 | 3206.34 |  |  | 19
1988-12-09 | 3206.05 |  |  | 19
1988-12-08 | 3205.93 |  |  | 19
1988-12-07 | 3205.79 |  |  | 19
1988-12-06 | 3205.71 |  |  | 19
1988-12-05 | 3205.63 |  |  | 20
1988-12-04 | 3205.56 |  |  | 20
1988-12-03 | 3205.44 |  |  | 20
1988-12-02 | 3205.36 |  |  | 20
1988-12-01 | 3205.23 |  |  | 20
1988-11-30 | 3205.15 |  |  | 20
1988-11-29 | 3205.03 |  |  | 20
1988-11-28 | 3204.88 |  |  | 20
1988-11-27 | 3204.79 |  |  | 20
1988-11-26 | 3204.67 |  |  | 20
1988-11-25 | 3204.52 |  |  | 20
1988-11-24 | 3204.34 |  |  | 20
1988-11-23 | 3203.98 |  |  | 19
1988-11-22 | 3203.66 |  |  | 20
1988-11-21 | 3203.57 |  |  | 27
1988-11-20 | 3203.49 |  |  | 31
1988-11-19 | 3203.42 |  |  | 31
1988-11-18 | 3203.36 |  |  | 31
1988-11-17 | 3203.23 |  |  | 31
1988-11-16 | 3203.14 |  |  | 31
1988-11-15 | 3203.03 |  |  | 31
1988-11-14 | 3202.96 |  |  | 31
1988-11-13 | 3202.88 |  |  | 31
1988-11-12 | 3202.8 |  |  | 31
1988-11-11 | 3202.76 |  |  | 31
1988-11-10 | 3202.68 |  |  | 31
1988-11-09 | 3202.64 |  |  | 31
1988-11-08 | 3202.58 |  |  | 31
1988-11-07 | 3202.58 |  |  | 31
1988-11-06 | 3202.58 |  |  | 31
1988-11-05 | 3202.58 |  |  | 31
1988-11-04 | 3202.51 |  |  | 31
1988-11-03 | 3202.46 |  |  | 31
1988-11-02 | 3202.45 |  |  | 31
1988-11-01 | 3202.45 |  |  | 31
1988-10-31 | 3202.45 |  |  | 31
1988-10-30 | 3202.46 |  |  | 31
1988-10-29 | 3202.46 |  |  | 31
1988-10-28 | 3202.46 |  |  | 31
1988-10-27 | 3202.48 |  |  | 31
1988-10-26 | 3202.49 |  |  | 31
1988-10-25 | 3202.51 |  |  | 31
1988-10-24 | 3202.51 |  |  | 28
1988-10-23 | 3202.53 |  |  | 30
1988-10-22 | 3202.53 |  |  | 30
1988-10-21 | 3202.53 |  |  | 30
1988-10-20 | 3202.55 |  |  | 30
1988-10-19 | 3202.58 |  |  | 30
1988-10-18 | 3202.58 |  |  | 30
1988-10-17 | 3202.59 |  |  | 30
1988-10-16 | 3202.59 |  |  | 30
1988-10-15 | 3202.59 |  |  | 30
1988-10-14 | 3202.59 |  |  | 44
1988-10-13 | 3202.63 |  |  | 63
1988-10-12 | 3202.69 |  |  | 67
1988-10-11 | 3202.73 |  |  | 84
1988-10-10 | 3202.83 |  |  | 112
1988-10-09 | 3202.95 |  |  | 123
1988-10-08 | 3203.05 |  |  | 123
1988-10-07 | 3203.17 |  |  | 135
1988-10-06 | 3203.27 |  |  | 154
1988-10-05 | 3203.4 |  |  | 154
1988-10-04 | 3203.54 |  |  | 154
1988-10-03 | 3203.68 |  |  | 154
1988-10-02 | 3203.8 |  |  | 154
1988-10-01 | 3203.95 |  |  | 154
1988-09-30 | 3204.12 |  |  | 155
1988-09-29 | 3204.22 |  |  | 154
1988-09-28 | 3204.34 |  |  | 154
1988-09-27 | 3204.47 |  |  | 154
1988-09-26 | 3204.61 |  |  | 154
1988-09-25 | 3204.76 |  |  | 154
1988-09-24 | 3204.9 |  |  | 154
1988-09-23 | 3205.02 |  |  | 141
1988-09-22 | 3205.16 |  |  | 126
1988-09-21 | 3205.28 |  |  | 126
1988-09-20 | 3205.38 |  |  | 165
1988-09-19 | 3205.54 |  |  | 195
1988-09-18 | 3205.73 |  |  | 194
1988-09-17 | 3205.92 |  |  | 195
1988-09-16 | 3206.12 |  |  | 194
1988-09-15 | 3206.35 |  |  | 194
1988-09-14 | 3206.58 |  |  | 194
1988-09-13 | 3206.72 |  |  | 194
1988-09-12 | 3206.93 |  |  | 207
1988-09-11 | 3207.09 |  |  | 221
1988-09-10 | 3207.3 |  |  | 221
1988-09-09 | 3207.57 |  |  | 241
1988-09-08 | 3207.82 |  |  | 295
1988-09-07 | 3208.1 |  |  | 329
1988-09-06 | 3208.46 |  |  | 329
1988-09-05 | 3208.79 |  |  | 329
1988-09-04 | 3209.12 |  |  | 331
1988-09-03 | 3209.42 |  |  | 331
1988-09-02 | 3209.72 |  |  | 331
1988-09-01 | 3210.03 |  |  | 331
1988-08-31 | 3210.32 |  |  | 331
1988-08-30 | 3210.65 |  |  | 331
1988-08-29 | 3210.95 |  |  | 332
1988-08-28 | 3211.28 |  |  | 332
1988-08-27 | 3211.57 |  |  | 334
1988-08-26 | 3211.88 |  |  | 334
1988-08-25 | 3212.18 |  |  | 334
1988-08-24 | 3212.5 |  |  | 334
1988-08-23 | 3212.79 |  |  | 334
1988-08-22 | 3213.09 |  |  | 334
1988-08-21 | 3213.37 |  |  | 334
1988-08-20 | 3213.66 |  |  | 335
1988-08-19 | 3213.98 |  |  | 337
1988-08-18 | 3214.21 |  |  | 337
1988-08-17 | 3214.52 |  |  | 337
1988-08-16 | 3214.85 |  |  | 337
1988-08-15 | 3215.2 |  |  | 337
1988-08-14 | 3215.48 |  |  | 337
1988-08-13 | 3215.76 |  |  | 338
1988-08-12 | 3216.04 |  |  | 338
1988-08-11 | 3216.36 |  |  | 339
1988-08-10 | 3216.64 |  |  | 340
1988-08-09 | 3216.91 |  |  | 340
1988-08-08 | 3217.17 |  |  | 340
1988-08-07 | 3217.47 |  |  | 340
1988-08-06 | 3217.74 |  |  | 340
1988-08-05 | 3218.07 |  |  | 342
1988-08-04 | 3218.42 |  |  | 342
1988-08-03 | 3218.68 |  |  | 342
1988-08-02 | 3218.91 |  |  | 342
1988-08-01 | 3219.23 |  |  | 342
1988-07-31 | 3219.5 |  |  | 342
1988-07-30 | 3219.8 |  |  | 342
1988-07-29 | 3220.06 |  |  | 331
1988-07-28 | 3220.33 |  |  | 313
1988-07-27 | 3220.6 |  |  | 313
1988-07-26 | 3220.86 |  |  | 313
1988-07-25 | 3221.13 |  |  | 313
1988-07-24 | 3221.37 |  |  | 313
1988-07-23 | 3221.61 |  |  | 314
1988-07-22 | 3221.86 |  |  | 315
1988-07-21 | 3222.1 |  |  | 315
1988-07-20 | 3222.33 |  |  | 315
1988-07-19 | 3222.56 |  |  | 315
1988-07-18 | 3222.77 |  |  | 315
1988-07-17 | 3222.99 |  |  | 315
1988-07-16 | 3223.23 |  |  | 315
1988-07-15 | 3223.42 |  |  | 315
1988-07-14 | 3223.69 |  |  | 315
1988-07-13 | 3223.93 |  |  | 315
1988-07-12 | 3224.2 |  |  | 317
1988-07-11 | 3224.43 |  |  | 318
1988-07-10 | 3224.67 |  |  | 318
1988-07-09 | 3224.94 |  |  | 318
1988-07-08 | 3225.13 |  |  | 318
1988-07-07 | 3225.3 |  |  | 318
1988-07-06 | 3225.5 |  |  | 318
1988-07-05 | 3225.72 |  |  | 318
1988-07-04 | 3225.95 |  |  | 284
1988-07-03 | 3226.18 |  |  | 236
1988-07-02 | 3226.36 |  |  | 237
1988-07-01 | 3226.52 |  |  | 237
1988-06-30 | 3226.65 |  |  | 236
1988-06-29 | 3226.78 |  |  | 236
1988-06-28 | 3226.96 |  |  | 237
1988-06-27 | 3227.16 |  |  | 238
1988-06-26 | 3227.38 |  |  | 238
1988-06-25 | 3227.55 |  |  | 238
1988-06-24 | 3227.69 |  |  | 238
1988-06-23 | 3227.83 |  |  | 238
1988-06-22 | 3228.02 |  |  | 238
1988-06-21 | 3228.17 |  |  | 238
1988-06-20 | 3228.32 |  |  | 238
1988-06-19 | 3228.48 |  |  | 238
1988-06-18 | 3228.6 |  |  | 238
1988-06-17 | 3228.73 |  |  | 238
1988-06-16 | 3228.85 |  |  | 238
1988-06-15 | 3229.01 |  |  | 238
1988-06-14 | 3229.09 |  |  | 238
1988-06-13 | 3229.22 |  |  | 238
1988-06-12 | 3229.31 |  |  | 238
1988-06-11 | 3229.45 |  |  | 238
1988-06-10 | 3229.52 |  |  | 252
1988-06-09 | 3229.61 |  |  | 273
1988-06-08 | 3229.73 |  |  | 273
1988-06-07 | 3229.82 |  |  | 273
1988-06-06 | 3229.89 |  |  | 273
1988-06-05 | 3230.01 |  |  | 273
1988-06-04 | 3230.12 |  |  | 273
1988-06-03 | 3230.27 |  |  | 273
1988-06-02 | 3230.37 |  |  | 273
1988-06-01 | 3230.5 |  |  | 273
1988-05-31 | 3230.64 |  |  | 273
1988-05-30 | 3230.79 |  |  | 273
1988-05-29 | 3230.93 |  |  | 273
1988-05-28 | 3231.11 |  |  | 274
1988-05-27 | 3231.27 |  |  | 280
1988-05-26 | 3231.39 |  |  | 290
1988-05-25 | 3231.59 |  |  | 290
1988-05-24 | 3231.75 |  |  | 290
1988-05-23 | 3231.89 |  |  | 251
1988-05-22 | 3232.05 |  |  | 229
1988-05-21 | 3232.16 |  |  | 228
1988-05-20 | 3232.28 |  |  | 229
1988-05-19 | 3232.37 |  |  | 230
1988-05-18 | 3232.47 |  |  | 230
1988-05-17 | 3232.59 |  |  | 230
1988-05-16 | 3232.68 |  |  | 229
1988-05-15 | 3232.76 |  |  | 229
1988-05-14 | 3232.84 |  |  | 228
1988-05-13 | 3232.94 |  |  | 229
1988-05-12 | 3232.98 |  |  | 221
1988-05-11 | 3232.99 |  |  | 209
1988-05-10 | 3232.96 |  |  | 209
1988-05-09 | 3232.9 |  |  | 209
1988-05-08 | 3232.89 |  |  | 209
1988-05-07 | 3232.86 |  |  | 209
1988-05-06 | 3232.82 |  |  | 209
1988-05-05 | 3232.75 |  |  | 209
1988-05-04 | 3232.67 |  |  | 209
1988-05-03 | 3232.66 |  |  | 209
1988-05-02 | 3232.65 |  |  | 209
1988-05-01 | 3232.6 |  |  | 209
1988-04-30 | 3232.54 |  |  | 209
1988-04-29 | 3232.48 |  |  | 209
1988-04-28 | 3232.35 |  |  | 208
1988-04-27 | 3232.25 |  |  | 207
1988-04-26 | 3232.09 |  |  | 207
1988-04-25 | 3231.91 |  |  | 207
1988-04-24 | 3231.67 |  |  | 207
1988-04-23 | 3231.36 |  |  | 207
1988-04-22 | 3230.94 |  |  | 207
1988-04-21 | 3230.49 |  |  | 207
1988-04-20 | 3230.14 |  |  | 206
1988-04-19 | 3229.91 |  |  | 205
1988-04-18 | 3229.68 |  |  | 205
1988-04-17 | 3229.5 |  |  | 205
1988-04-16 | 3229.5 |  |  | 205
1988-04-15 | 3229.42 |  |  | 205
1988-04-14 | 3229.33 |  |  | 205
1988-04-13 | 3229.33 |  |  | 205
1988-04-12 | 3229.3 |  |  | 205
1988-04-11 | 3229.29 |  |  | 205
1988-04-10 | 3229.27 |  |  | 205
1988-04-09 | 3229.24 |  |  | 205
1988-04-08 | 3229.19 |  |  | 175
1988-04-07 | 3229.15 |  |  | 154
1988-04-06 | 3229.08 |  |  | 155
1988-04-05 | 3228.93 |  |  | 155
1988-04-04 | 3228.79 |  |  | 156
1988-04-03 | 3228.61 |  |  | 110
1988-04-02 | 3228.47 |  |  | 82
1988-04-01 | 3228.31 |  |  | 82
1988-03-31 | 3228.18 |  |  | 61
1988-03-30 | 3227.95 |  |  | 32
1988-03-29 | 3227.76 |  |  | 32
1988-03-28 | 3227.59 |  |  | 32
1988-03-27 | 3227.37 |  |  | 32
1988-03-26 | 3227.21 |  |  | 32
1988-03-25 | 3226.99 |  |  | 32
1988-03-24 | 3226.78 |  |  | 32
1988-03-23 | 3226.54 |  |  | 32
1988-03-22 | 3226.33 |  |  | 32
1988-03-21 | 3226.13 |  |  | 32
1988-03-20 | 3225.95 |  |  | 32
1988-03-19 | 3225.77 |  |  | 32
1988-03-18 | 3225.58 |  |  | 32
1988-03-17 | 3225.41 |  |  | 32
1988-03-16 | 3225.25 |  |  | 32
1988-03-15 | 3225.11 |  |  | 32
1988-03-14 | 3224.88 |  |  | 32
1988-03-13 | 3224.69 |  |  | 32
1988-03-12 | 3224.46 |  |  | 32
1988-03-11 | 3224.19 |  |  | 32
1988-03-10 | 3223.89 |  |  | 32
1988-03-09 | 3223.47 |  |  | 32
1988-03-08 | 3223.15 |  |  | 32
1988-03-07 | 3222.76 |  |  | 32
1988-03-06 | 3222.28 |  |  | 32
1988-03-05 | 3221.63 |  |  | 32
1988-03-04 | 3220.97 |  |  | 32
1988-03-03 | 3220.37 |  |  | 32
1988-03-02 | 3219.74 |  |  | 32
1988-03-01 | 3219.05 |  |  | 32
1988-02-29 | 3218.43 |  |  | 32
1988-02-28 | 3217.84 |  |  | 32
1988-02-27 | 3217.45 |  |  | 32
1988-02-26 | 3217.03 |  |  | 32
1988-02-25 | 3216.77 |  |  | 32
1988-02-24 | 3216.5 |  |  | 32
1988-02-23 | 3216.21 |  |  | 31
1988-02-22 | 3215.92 |  |  | 31
1988-02-21 | 3215.63 |  |  | 31
1988-02-20 | 3215.41 |  |  | 31
1988-02-19 | 3215.16 |  |  | 31
1988-02-18 | 3214.96 |  |  | 31
1988-02-17 | 3214.78 |  |  | 31
1988-02-16 | 3214.43 |  |  | 31
1988-02-15 | 3214.13 |  |  | 31
1988-02-14 | 3213.83 |  |  | 31
1988-02-13 | 3213.43 |  |  | 31
1988-02-12 | 3212.94 |  |  | 31
1988-02-11 | 3212.44 |  |  | 30
1988-02-10 | 3211.83 |  |  | 30
1988-02-09 | 3211.27 |  |  | 30
1988-02-08 | 3210.86 |  |  | 30
1988-02-07 | 3210.72 |  |  | 30
1988-02-06 | 3210.62 |  |  | 30
1988-02-05 | 3210.52 |  |  | 30
1988-02-04 | 3210.45 |  |  | 30
1988-02-03 | 3210.36 |  |  | 30
1988-02-02 | 3210.28 |  |  | 30
1988-02-01 | 3210.18 |  |  | 31
1988-01-31 | 3210.05 |  |  | 31
1988-01-30 | 3209.91 |  |  | 31
1988-01-29 | 3209.75 |  |  | 31
1988-01-28 | 3209.57 |  |  | 31
1988-01-27 | 3209.53 |  |  | 31
1988-01-26 | 3209.43 |  |  | 31
1988-01-25 | 3209.31 |  |  | 31
1988-01-24 | 3209.19 |  |  | 31
1988-01-23 | 3209.1 |  |  | 31
1988-01-22 | 3209 |  |  | 31
1988-01-21 | 3208.89 |  |  | 31
1988-01-20 | 3208.76 |  |  | 30
1988-01-19 | 3208.64 |  |  | 30
1988-01-18 | 3208.48 |  |  | 30
1988-01-17 | 3208.32 |  |  | 30
1988-01-16 | 3208.07 |  |  | 30
1988-01-15 | 3207.85 |  |  | 30
1988-01-14 | 3207.67 |  |  | 30
1988-01-13 | 3207.5 |  |  | 29
1988-01-12 | 3207.37 |  |  | 29
1988-01-11 | 3207.19 |  |  | 29
1988-01-10 | 3207.08 |  |  | 29
1988-01-09 | 3206.92 |  |  | 29
1988-01-08 | 3206.83 |  |  | 29
1988-01-07 | 3206.75 |  |  | 29
1988-01-06 | 3206.69 |  |  | 29
1988-01-05 | 3206.6 |  |  | 29
1988-01-04 | 3206.54 |  |  | 29
1988-01-03 | 3206.49 |  |  | 29
1988-01-02 | 3206.46 |  |  | 29
1988-01-01 | 3206.4 |  |  | 29
1987-12-31 | 3206.36 |  |  | 29
1987-12-30 | 3206.28 |  |  | 29
1987-12-29 | 3206.24 |  |  | 29
1987-12-28 | 3206.17 |  |  | 28
1987-12-27 | 3206.09 |  |  | 28
1987-12-26 | 3206.04 |  |  | 28
1987-12-25 | 3206.01 |  |  | 27
1987-12-24 | 3206 |  |  | 27
1987-12-23 | 3205.96 |  |  | 28
1987-12-22 | 3205.91 |  |  | 28
1987-12-21 | 3205.81 |  |  | 28
1987-12-20 | 3205.72 |  |  | 28
1987-12-19 | 3205.7 |  |  | 28
1987-12-18 | 3205.63 |  |  | 27
1987-12-17 | 3205.55 |  |  | 25
1987-12-16 | 3205.43 |  |  | 25
1987-12-15 | 3205.34 |  |  | 25
1987-12-14 | 3205.29 |  |  | 15
1987-12-13 | 3205.16 |  |  | 11
1987-12-12 | 3205.04 |  |  | 11
1987-12-11 | 3204.86 |  |  | 11
1987-12-10 | 3204.64 |  |  | 11
1987-12-09 | 3204.45 |  |  | 11
1987-12-08 | 3204.32 |  |  | 11
1987-12-07 | 3204.23 |  |  | 11
1987-12-06 | 3204.06 |  |  | 11
1987-12-05 | 3203.96 |  |  | 11
1987-12-04 | 3203.8 |  |  | 8.3
1987-12-03 | 3203.69 |  |  | 11
1987-12-02 | 3203.56 |  |  | 11
1987-12-01 | 3203.48 |  |  | 11
1987-11-30 | 3203.36 |  |  | 11
1987-11-29 | 3203.27 |  |  | 11
1987-11-28 | 3203.2 |  |  | 11
1987-11-27 | 3203.09 |  |  | 11
1987-11-26 | 3203.04 |  |  | 11
1987-11-25 | 3202.98 |  |  | 11
1987-11-24 | 3202.9 |  |  | 11
1987-11-23 | 3202.8 |  |  | 11
1987-11-22 | 3202.72 |  |  | 12
1987-11-21 | 3202.64 |  |  | 12
1987-11-20 | 3202.56 |  |  | 12
1987-11-19 | 3202.47 |  |  | 12
1987-11-18 | 3202.41 |  |  | 12
1987-11-17 | 3202.33 |  |  | 12
1987-11-16 | 3202.24 |  |  | 12
1987-11-15 | 3202.17 |  |  | 12
1987-11-14 | 3202.08 |  |  | 12
1987-11-13 | 3202 |  |  | 12
1987-11-12 | 3201.93 |  |  | 12
1987-11-11 | 3201.84 |  |  | 12
1987-11-10 | 3201.77 |  |  | 12
1987-11-09 | 3201.69 |  |  | 12
1987-11-08 | 3201.62 |  |  | 13
1987-11-07 | 3201.58 |  |  | 13
1987-11-06 | 3201.5 |  |  | 13
1987-11-05 | 3201.49 |  |  | 12
1987-11-04 | 3201.39 |  |  | 12
1987-11-03 | 3201.35 |  |  | 14
1987-11-02 | 3201.29 |  |  | 21
1987-11-01 | 3201.24 |  |  | 25
1987-10-31 | 3201.2 |  |  | 26
1987-10-30 | 3201.18 |  |  | 25
1987-10-29 | 3201.12 |  |  | 25
1987-10-28 | 3201.1 |  |  | 20
1987-10-27 | 3201.04 |  |  | 16
1987-10-26 | 3201 |  |  | 44
1987-10-25 | 3201.04 |  |  | 83
1987-10-24 | 3201.04 |  |  | 83
1987-10-23 | 3201.04 |  |  | 83
1987-10-22 | 3201.05 |  |  | 82
1987-10-21 | 3201.05 |  |  | 124
1987-10-20 | 3201.17 |  |  | 173
1987-10-19 | 3201.26 |  |  | 198
1987-10-18 | 3201.41 |  |  | 232
1987-10-17 | 3201.63 |  |  | 232
1987-10-16 | 3201.82 |  |  | 256
1987-10-15 | 3202 |  |  | 280
1987-10-14 | 3202.25 |  |  | 309
1987-10-13 | 3202.52 |  |  | 337
1987-10-12 | 3202.82 |  |  | 376
1987-10-11 | 3203.15 |  |  | 424
1987-10-10 | 3203.54 |  |  | 423
1987-10-09 | 3203.93 |  |  | 471
1987-10-08 | 3204.37 |  |  | 514
1987-10-07 | 3204.86 |  |  | 517
1987-10-06 | 3205.34 |  |  | 518
1987-10-05 | 3205.79 |  |  | 518
1987-10-04 | 3206.25 |  |  | 518
1987-10-03 | 3206.72 |  |  | 518
1987-10-02 | 3207.18 |  |  | 521
1987-10-01 | 3207.66 |  |  | 522
1987-09-30 | 3208.1 |  |  | 522
1987-09-29 | 3208.56 |  |  | 522
1987-09-28 | 3209 |  |  | 524
1987-09-27 | 3209.43 |  |  | 526
1987-09-26 | 3209.89 |  |  | 526
1987-09-25 | 3210.37 |  |  | 486
1987-09-24 | 3210.82 |  |  | 432
1987-09-23 | 3211.2 |  |  | 429
1987-09-22 | 3211.59 |  |  | 429
1987-09-21 | 3211.92 |  |  | 427
1987-09-20 | 3212.29 |  |  | 423
1987-09-19 | 3212.63 |  |  | 421
1987-09-18 | 3212.97 |  |  | 390
1987-09-17 | 3213.29 |  |  | 334
1987-09-16 | 3213.6 |  |  | 331
1987-09-15 | 3213.89 |  |  | 329
1987-09-14 | 3214.23 |  |  | 299
1987-09-13 | 3214.57 |  |  | 274
1987-09-12 | 3214.78 |  |  | 273
1987-09-11 | 3215.07 |  |  | 259
1987-09-10 | 3215.27 |  |  | 236
1987-09-09 | 3215.42 |  |  | 236
1987-09-08 | 3215.61 |  |  | 236
1987-09-07 | 3215.82 |  |  | 236
1987-09-06 | 3216.03 |  |  | 236
1987-09-05 | 3216.2 |  |  | 236
1987-09-04 | 3216.39 |  |  | 236
1987-09-03 | 3216.67 |  |  | 236
1987-09-02 | 3216.87 |  |  | 236
1987-09-01 | 3217.11 |  |  | 236
1987-08-31 | 3217.32 |  |  | 236
1987-08-30 | 3217.53 |  |  | 236
1987-08-29 | 3217.71 |  |  | 236
1987-08-28 | 3217.86 |  |  | 236
1987-08-27 | 3218.06 |  |  | 236
1987-08-26 | 3218.28 |  |  | 236
1987-08-25 | 3218.48 |  |  | 236
1987-08-24 | 3218.66 |  |  | 236
1987-08-23 | 3218.85 |  |  | 236
1987-08-22 | 3219.02 |  |  | 236
1987-08-21 | 3219.24 |  |  | 236
1987-08-20 | 3219.44 |  |  | 236
1987-08-19 | 3219.67 |  |  | 236
1987-08-18 | 3219.82 |  |  | 236
1987-08-17 | 3220.04 |  |  | 236
1987-08-16 | 3220.19 |  |  | 236
1987-08-15 | 3220.4 |  |  | 236
1987-08-14 | 3220.62 |  |  | 236
1987-08-13 | 3220.8 |  |  | 236
1987-08-12 | 3221 |  |  | 236
1987-08-11 | 3221.22 |  |  | 236
1987-08-10 | 3221.42 |  |  | 236
1987-08-09 | 3221.62 |  |  | 236
1987-08-08 | 3221.83 |  |  | 236
1987-08-07 | 3221.97 |  |  | 229
1987-08-06 | 3222.15 |  |  | 222
1987-08-05 | 3222.3 |  |  | 221
1987-08-04 | 3222.5 |  |  | 219
1987-08-03 | 3222.66 |  |  | 221
1987-08-02 | 3222.79 |  |  | 221
1987-08-01 | 3222.92 |  |  | 221
1987-07-31 | 3223.12 |  |  | 221
1987-07-30 | 3223.26 |  |  | 242
1987-07-29 | 3223.39 |  |  | 273
1987-07-28 | 3223.65 |  |  | 273
1987-07-27 | 3223.78 |  |  | 273
1987-07-26 | 3223.94 |  |  | 273
1987-07-25 | 3224.06 |  |  | 273
1987-07-24 | 3224.08 |  |  | 273
1987-07-23 | 3224.09 |  |  | 273
1987-07-22 | 3223.96 |  |  | 275
1987-07-21 | 3223.93 |  |  | 273
1987-07-20 | 3224.11 |  |  | 273
1987-07-19 | 3224.24 |  |  | 274
1987-07-18 | 3224.39 |  |  | 275
1987-07-17 | 3224.54 |  |  | 276
1987-07-16 | 3224.75 |  |  | 275
1987-07-15 | 3225.03 |  |  | 275
1987-07-14 | 3225.23 |  |  | 275
1987-07-13 | 3225.42 |  |  | 275
1987-07-12 | 3225.58 |  |  | 275
1987-07-11 | 3225.79 |  |  | 275
1987-07-10 | 3225.97 |  |  | 275
1987-07-09 | 3226.18 |  |  | 275
1987-07-08 | 3226.21 |  |  | 275
1987-07-07 | 3226.38 |  |  | 275
1987-07-06 | 3226.58 |  |  | 278
1987-07-05 | 3226.82 |  |  | 278
1987-07-04 | 3227.04 |  |  | 279
1987-07-03 | 3227.24 |  |  | 280
1987-07-02 | 3227.4 |  |  | 280
1987-07-01 | 3227.56 |  |  | 267
1987-06-30 | 3227.73 |  |  | 254
1987-06-29 | 3227.89 |  |  | 254
1987-06-28 | 3228.1 |  |  | 254
1987-06-27 | 3228.22 |  |  | 254
1987-06-26 | 3228.43 |  |  | 270
1987-06-25 | 3228.58 |  |  | 251
1987-06-24 | 3228.75 |  |  | 226
1987-06-23 | 3228.87 |  |  | 226
1987-06-22 | 3229 |  |  | 226
1987-06-21 | 3229.13 |  |  | 226
1987-06-20 | 3229.25 |  |  | 226
1987-06-19 | 3229.34 |  |  | 227
1987-06-18 | 3229.53 |  |  | 228
1987-06-17 | 3229.61 |  |  | 228
1987-06-16 | 3229.68 |  |  | 228
1987-06-15 | 3229.84 |  |  | 228
1987-06-14 | 3230 |  |  | 228
1987-06-13 | 3230.12 |  |  | 228
1987-06-12 | 3230.23 |  |  | 228
1987-06-11 | 3230.36 |  |  | 228
1987-06-10 | 3230.45 |  |  | 228
1987-06-09 | 3230.55 |  |  | 229
1987-06-08 | 3230.65 |  |  | 228
1987-06-07 | 3230.72 |  |  | 229
1987-06-06 | 3230.89 |  |  | 228
1987-06-05 | 3231 |  |  | 229
1987-06-04 | 3231.15 |  |  | 229
1987-06-03 | 3231.26 |  |  | 231
1987-06-02 | 3231.36 |  |  | 231
1987-06-01 | 3231.44 |  |  | 231
1987-05-31 | 3231.56 |  |  | 243
1987-05-30 | 3231.71 |  |  | 252
1987-05-29 | 3231.87 |  |  | 270
1987-05-28 | 3232.04 |  |  | 293
1987-05-27 | 3232.17 |  |  | 293
1987-05-26 | 3232.29 |  |  | 293
1987-05-25 | 3232.42 |  |  | 293
1987-05-24 | 3232.58 |  |  | 293
1987-05-23 | 3232.69 |  |  | 293
1987-05-22 | 3232.88 |  |  | 317
1987-05-21 | 3233.05 |  |  | 357
1987-05-20 | 3233.22 |  |  | 357
1987-05-19 | 3233.43 |  |  | 361
1987-05-18 | 3233.71 |  |  | 361
1987-05-17 | 3233.86 |  |  | 361
1987-05-16 | 3234.1 |  |  | 361
1987-05-15 | 3234.27 |  |  | 361
1987-05-14 | 3234.43 |  |  | 361
1987-05-13 | 3234.62 |  |  | 361
1987-05-12 | 3234.77 |  |  | 361
1987-05-11 | 3234.96 |  |  | 363
1987-05-10 | 3235.13 |  |  | 368
1987-05-09 | 3235.21 |  |  | 375
1987-05-08 | 3235.33 |  |  | 380
1987-05-07 | 3235.44 |  |  | 387
1987-05-06 | 3235.46 |  |  | 306
1987-05-05 | 3235.4 |  |  | 346
1987-05-04 | 3235.4 |  |  | 396
1987-05-03 | 3235.36 |  |  | 395
1987-05-02 | 3235.29 |  |  | 389
1987-05-01 | 3235.13 |  |  | 378
1987-04-30 | 3235.06 |  |  | 374
1987-04-29 | 3235.03 |  |  | 374
1987-04-28 | 3235.03 |  |  | 405
1987-04-27 | 3235.03 |  |  | 457
1987-04-26 | 3235.03 |  |  | 457
1987-04-25 | 3235.03 |  |  | 457
1987-04-24 | 3235.03 |  |  | 735
1987-04-23 | 3235.23 |  |  | 971
1987-04-22 | 3235.44 |  |  | 990
1987-04-21 | 3235.72 |  |  | 1010
1987-04-20 | 3235.96 |  |  | 1040
1987-04-19 | 3236.15 |  |  | 1060
1987-04-18 | 3236.34 |  |  | 1080
1987-04-17 | 3236.45 |  |  | 1090
1987-04-16 | 3236.56 |  |  | 1100
1987-04-15 | 3236.64 |  |  | 1120
1987-04-14 | 3236.73 |  |  | 1130
1987-04-13 | 3236.87 |  |  | 1150
1987-04-12 | 3236.89 |  |  | 1170
1987-04-11 | 3236.88 |  |  | 1150
1987-04-10 | 3236.79 |  |  | 1060
1987-04-09 | 3236.65 |  |  | 958
1987-04-08 | 3236.44 |  |  | 923
1987-04-07 | 3236.17 |  |  | 686
1987-04-06 | 3235.83 |  |  | 483
1987-04-05 | 3235.19 |  |  | 338
1987-04-04 | 3233.67 |  |  | 271
1987-04-03 | 3233.67 |  |  | 270
1987-04-02 | 3233.21 |  |  | 268
1987-04-01 | 3232.59 |  |  | 454
1987-03-31 | 3232.42 |  |  | 614
1987-03-30 | 3232.45 |  |  | 614
1987-03-29 | 3232.5 |  |  | 614
1987-03-28 | 3232.6 |  |  | 614
1987-03-27 | 3232.6 |  |  | 725
1987-03-26 | 3232.7 |  |  | 815
1987-03-25 | 3232.84 |  |  | 815
1987-03-24 | 3232.9 |  |  | 1220
1987-03-23 | 3233.23 |  |  | 1430
1987-03-22 | 3233.72 |  |  | 1430
1987-03-21 | 3234.13 |  |  | 1440
1987-03-20 | 3234.51 |  |  | 1330
1987-03-19 | 3234.73 |  |  | 1170
1987-03-18 | 3234.69 |  |  | 974
1987-03-17 | 3234.49 |  |  | 794
1987-03-16 | 3234.15 |  |  | 659
1987-03-15 | 3233.5 |  |  | 463
1987-03-14 | 3232.44 |  |  | 460
1987-03-13 | 3230.98 |  |  | 257
1987-03-12 | 3228.7 |  |  | 88
1987-03-11 | 3227.24 |  |  | 87
1987-03-10 | 3226.64 |  |  | 87
1987-03-09 | 3225.82 |  |  | 87
1987-03-08 | 3224.96 |  |  | 86
1987-03-07 | 3223.83 |  |  | 86
1987-03-06 | 3222.17 |  |  | 47
1987-03-05 | 3219.96 |  |  | 20
1987-03-04 | 3218.18 |  |  | 20
1987-03-03 | 3217.34 |  |  | 20
1987-03-02 | 3217.08 |  |  | 19
1987-03-01 | 3216.91 |  |  | 19
1987-02-28 | 3216.74 |  |  | 35
1987-02-27 | 3216.56 |  |  | 51
1987-02-26 | 3216.39 |  |  | 51
1987-02-25 | 3216.26 |  |  | 51
1987-02-24 | 3216.09 |  |  | 51
1987-02-23 | 3215.91 |  |  | 51
1987-02-22 | 3215.69 |  |  | 51
1987-02-21 | 3215.42 |  |  | 51
1987-02-20 | 3215.08 |  |  | 154
1987-02-19 | 3214.94 |  |  | 241
1987-02-18 | 3214.79 |  |  | 241
1987-02-17 | 3214.54 |  |  | 240
1987-02-16 | 3214.29 |  |  | 239
1987-02-15 | 3213.96 |  |  | 239
1987-02-14 | 3213.44 |  |  | 238
1987-02-13 | 3212.61 |  |  | 236
1987-02-12 | 3212.27 |  |  | 236
1987-02-11 | 3212.01 |  |  | 236
1987-02-10 | 3211.91 |  |  | 236
1987-02-09 | 3211.91 |  |  | 407
1987-02-08 | 3212.09 |  |  | 502
1987-02-07 | 3212.28 |  |  | 502
1987-02-06 | 3212.44 |  |  | 489
1987-02-05 | 3212.6 |  |  | 478
1987-02-04 | 3212.66 |  |  | 478
1987-02-03 | 3212.66 |  |  | 478
1987-02-02 | 3212.65 |  |  | 482
1987-02-01 | 3212.72 |  |  | 482
1987-01-31 | 3212.86 |  |  | 482
1987-01-30 | 3212.97 |  |  | 482
1987-01-29 | 3212.98 |  |  | 287
1987-01-28 | 3212.62 |  |  | 25
1987-01-27 | 3211.68 |  |  | 25
1987-01-26 | 3210.91 |  |  | 25
1987-01-25 | 3210.73 |  |  | 25
1987-01-24 | 3210.6 |  |  | 25
1987-01-23 | 3210.54 |  |  | 42
1987-01-22 | 3210.47 |  |  | 66
1987-01-21 | 3210.44 |  |  | 66
1987-01-20 | 3210.43 |  |  | 66
1987-01-19 | 3210.43 |  |  | 66
1987-01-18 | 3210.43 |  |  | 66
1987-01-17 | 3210.43 |  |  | 66
1987-01-16 | 3210.43 |  |  | 85
1987-01-15 | 3210.48 |  |  | 97
1987-01-14 | 3210.48 |  |  | 97
1987-01-13 | 3210.48 |  |  | 97
1987-01-12 | 3210.48 |  |  | 97
1987-01-11 | 3210.48 |  |  | 97
1987-01-10 | 3210.48 |  |  | 97
1987-01-09 | 3210.49 |  |  | 103
1987-01-08 | 3210.53 |  |  | 107
1987-01-07 | 3210.53 |  |  | 107
1987-01-06 | 3210.5 |  |  | 107
1987-01-05 | 3210.5 |  |  | 107
1987-01-04 | 3210.5 |  |  | 107
1987-01-03 | 3210.49 |  |  | 107
1987-01-02 | 3210.49 |  |  | 107
1987-01-01 | 3210.46 |  |  | 107
1986-12-31 | 3210.44 |  |  | 107
1986-12-30 | 3210.44 |  |  | 107
1986-12-29 | 3210.44 |  |  | 107
1986-12-28 | 3210.44 |  |  | 107
1986-12-27 | 3210.44 |  |  | 107
1986-12-26 | 3210.44 |  |  | 135
1986-12-25 | 3210.47 |  |  | 156
1986-12-24 | 3210.52 |  |  | 156
1986-12-23 | 3210.55 |  |  | 156
1986-12-22 | 3210.62 |  |  | 156
1986-12-21 | 3210.65 |  |  | 156
1986-12-20 | 3210.65 |  |  | 156
1986-12-19 | 3210.65 |  |  | 171
1986-12-18 | 3210.75 |  |  | 182
1986-12-17 | 3210.86 |  |  | 182
1986-12-16 | 3210.94 |  |  | 182
1986-12-15 | 3211.01 |  |  | 182
1986-12-14 | 3211.06 |  |  | 182
1986-12-13 | 3211.08 |  |  | 182
1986-12-12 | 3211.09 |  |  | 182
1986-12-11 | 3211.16 |  |  | 182
1986-12-10 | 3211.25 |  |  | 182
1986-12-09 | 3211.31 |  |  | 182
1986-12-08 | 3211.38 |  |  | 182
1986-12-07 | 3211.48 |  |  | 182
1986-12-06 | 3211.48 |  |  | 182
1986-12-05 | 3211.49 |  |  | 182
1986-12-04 | 3211.55 |  |  | 182
1986-12-03 | 3211.58 |  |  | 182
1986-12-02 | 3211.58 |  |  | 182
1986-12-01 | 3211.59 |  |  | 182
1986-11-30 | 3211.59 |  |  | 172
1986-11-29 | 3211.53 |  |  | 165
1986-11-28 | 3211.52 |  |  | 165
1986-11-27 | 3211.52 |  |  | 165
1986-11-26 | 3211.52 |  |  | 165
1986-11-25 | 3211.52 |  |  | 165
1986-11-24 | 3211.52 |  |  | 165
1986-11-23 | 3211.52 |  |  | 165
1986-11-22 | 3211.52 |  |  | 165
1986-11-21 | 3211.52 |  |  | 137
1986-11-20 | 3211.47 |  |  | 121
1986-11-19 | 3211.44 |  |  | 121
1986-11-18 | 3211.43 |  |  | 121
1986-11-17 | 3211.39 |  |  | 121
1986-11-16 | 3211.38 |  |  | 121
1986-11-15 | 3211.37 |  |  | 121
1986-11-14 | 3211.36 |  |  | 112
1986-11-13 | 3211.33 |  |  | 106
1986-11-12 | 3211.28 |  |  | 106
1986-11-11 | 3211.28 |  |  | 106
1986-11-10 | 3211.27 |  |  | 106
1986-11-09 | 3211.26 |  |  | 106
1986-11-08 | 3211.26 |  |  | 106
1986-11-07 | 3211.25 |  |  | 97
1986-11-06 | 3211.25 |  |  | 91
1986-11-05 | 3211.25 |  |  | 91
1986-11-04 | 3211.2 |  |  | 91
1986-11-03 | 3211.19 |  |  | 91
1986-11-02 | 3211.19 |  |  | 91
1986-11-01 | 3211.18 |  |  | 91
1986-10-31 | 3211.18 |  |  | 66
1986-10-30 | 3211.17 |  |  | 44
1986-10-29 | 3211.07 |  |  | 44
1986-10-28 | 3210.98 |  |  | 44
1986-10-27 | 3210.95 |  |  | 44
1986-10-26 | 3210.93 |  |  | 44
1986-10-25 | 3210.89 |  |  | 43
1986-10-24 | 3210.86 |  |  | 44
1986-10-23 | 3210.81 |  |  | 45
1986-10-22 | 3210.8 |  |  | 45
1986-10-21 | 3210.79 |  |  | 69
1986-10-20 | 3210.83 |  |  | 90
1986-10-19 | 3210.83 |  |  | 90
1986-10-18 | 3210.83 |  |  | 90
1986-10-17 | 3210.83 |  |  | 142
1986-10-16 | 3210.99 |  |  | 189
1986-10-15 | 3211.06 |  |  | 189
1986-10-14 | 3211.18 |  |  | 189
1986-10-13 | 3211.25 |  |  | 188
1986-10-12 | 3211.35 |  |  | 187
1986-10-11 | 3211.47 |  |  | 187
1986-10-10 | 3211.59 |  |  | 187
1986-10-09 | 3211.7 |  |  | 187
1986-10-08 | 3211.81 |  |  | 187
1986-10-07 | 3211.93 |  |  | 187
1986-10-06 | 3212.01 |  |  | 187
1986-10-05 | 3212.1 |  |  | 187
1986-10-04 | 3212.19 |  |  | 187
1986-10-03 | 3212.26 |  |  | 187
1986-10-02 | 3212.38 |  |  | 187
1986-10-01 | 3212.47 |  |  | 187
1986-09-30 | 3212.55 |  |  | 187
1986-09-29 | 3212.66 |  |  | 187
1986-09-28 | 3212.75 |  |  | 187
1986-09-27 | 3212.85 |  |  | 187
1986-09-26 | 3212.92 |  |  | 236
1986-09-25 | 3213.09 |  |  | 283
1986-09-24 | 3213.28 |  |  | 283
1986-09-23 | 3213.47 |  |  | 283
1986-09-22 | 3213.68 |  |  | 283
1986-09-21 | 3213.91 |  |  | 283
1986-09-20 | 3214.12 |  |  | 283
1986-09-19 | 3214.28 |  |  | 283
1986-09-18 | 3214.58 |  |  | 283
1986-09-17 | 3214.79 |  |  | 283
1986-09-16 | 3215.09 |  |  | 283
1986-09-15 | 3215.27 |  |  | 283
1986-09-14 | 3215.47 |  |  | 283
1986-09-13 | 3215.68 |  |  | 284
1986-09-12 | 3215.9 |  |  | 263
1986-09-11 | 3216.13 |  |  | 239
1986-09-10 | 3216.32 |  |  | 239
1986-09-09 | 3216.55 |  |  | 240
1986-09-08 | 3216.74 |  |  | 240
1986-09-07 | 3216.96 |  |  | 239
1986-09-06 | 3217.19 |  |  | 240
1986-09-05 | 3217.42 |  |  | 239
1986-09-04 | 3217.59 |  |  | 239
1986-09-03 | 3217.77 |  |  | 241
1986-09-02 | 3217.95 |  |  | 241
1986-09-01 | 3218.11 |  |  | 241
1986-08-31 | 3218.31 |  |  | 241
1986-08-30 | 3218.5 |  |  | 241
1986-08-29 | 3218.5 |  |  | 241
1986-08-28 | 3218.93 |  |  | 241
1986-08-27 | 3219.12 |  |  | 241
1986-08-26 | 3219.33 |  |  | 241
1986-08-25 | 3219.52 |  |  | 241
1986-08-24 | 3219.7 |  |  | 241
1986-08-23 | 3219.9 |  |  | 241
1986-08-22 | 3220.14 |  |  | 241
1986-08-21 | 3220.31 |  |  | 241
1986-08-20 | 3220.51 |  |  | 241
1986-08-19 | 3220.72 |  |  | 241
1986-08-18 | 3220.92 |  |  | 243
1986-08-17 | 3221.13 |  |  | 243
1986-08-16 | 3221.3 |  |  | 243
1986-08-15 | 3221.5 |  |  | 243
1986-08-14 | 3221.69 |  |  | 243
1986-08-13 | 3221.88 |  |  | 243
1986-08-12 | 3222.08 |  |  | 243
1986-08-11 | 3222.25 |  |  | 243
1986-08-10 | 3222.48 |  |  | 243
1986-08-09 | 3222.7 |  |  | 243
1986-08-08 | 3222.87 |  |  | 243
1986-08-07 | 3223.07 |  |  | 243
1986-08-06 | 3223.25 |  |  | 243
1986-08-05 | 3223.39 |  |  | 243
1986-08-04 | 3223.64 |  |  | 243
1986-08-03 | 3223.79 |  |  | 243
1986-08-02 | 3224.01 |  |  | 243
1986-08-01 | 3224.18 |  |  | 243
1986-07-31 | 3224.3 |  |  | 243
1986-07-30 | 3224.46 |  |  | 243
1986-07-29 | 3224.63 |  |  | 243
1986-07-28 | 3224.81 |  |  | 243
1986-07-27 | 3224.99 |  |  | 243
1986-07-26 | 3225.18 |  |  | 243
1986-07-25 | 3225.37 |  |  | 265
1986-07-24 | 3225.54 |  |  | 285
1986-07-23 | 3225.79 |  |  | 285
1986-07-22 | 3225.97 |  |  | 285
1986-07-21 | 3226.25 |  |  | 285
1986-07-20 | 3226.4 |  |  | 285
1986-07-19 | 3226.62 |  |  | 285
1986-07-18 | 3226.76 |  |  | 285
1986-07-17 | 3226.93 |  |  | 285
1986-07-16 | 3227.09 |  |  | 285
1986-07-15 | 3227.3 |  |  | 285
1986-07-14 | 3227.49 |  |  | 313
1986-07-13 | 3227.75 |  |  | 345
1986-07-12 | 3227.96 |  |  | 345
1986-07-11 | 3228.18 |  |  | 310
1986-07-10 | 3228.4 |  |  | 264
1986-07-09 | 3228.6 |  |  | 264
1986-07-08 | 3228.77 |  |  | 264
1986-07-07 | 3228.94 |  |  | 264
1986-07-06 | 3229.13 |  |  | 264
1986-07-05 | 3229.22 |  |  | 264
1986-07-04 | 3229.4 |  |  | 264
1986-07-03 | 3229.61 |  |  | 264
1986-07-02 | 3229.74 |  |  | 264
1986-07-01 | 3229.94 |  |  | 264
1986-06-30 | 3230.09 |  |  | 264
1986-06-29 | 3230.27 |  |  | 264
1986-06-28 | 3230.42 |  |  | 264
1986-06-27 | 3230.63 |  |  | 264
1986-06-26 | 3230.77 |  |  | 265
1986-06-25 | 3230.97 |  |  | 265
1986-06-24 | 3231.12 |  |  | 266
1986-06-23 | 3231.29 |  |  | 265
1986-06-22 | 3231.42 |  |  | 266
1986-06-21 | 3231.58 |  |  | 266
1986-06-20 | 3231.75 |  |  | 266
1986-06-19 | 3231.93 |  |  | 266
1986-06-18 | 3232.07 |  |  | 266
1986-06-17 | 3232.28 |  |  | 266
1986-06-16 | 3232.41 |  |  | 266
1986-06-15 | 3232.6 |  |  | 266
1986-06-14 | 3232.75 |  |  | 267
1986-06-13 | 3233 |  |  | 266
1986-06-12 | 3233.11 |  |  | 266
1986-06-11 | 3233.23 |  |  | 266
1986-06-10 | 3233.37 |  |  | 261
1986-06-09 | 3233.5 |  |  | 252
1986-06-08 | 3233.6 |  |  | 252
1986-06-07 | 3233.73 |  |  | 252
1986-06-06 | 3233.87 |  |  | 254
1986-06-05 | 3234.02 |  |  | 256
1986-06-04 | 3234.15 |  |  | 259
1986-06-03 | 3234.24 |  |  | 259
1986-06-02 | 3234.34 |  |  | 259
1986-06-01 | 3234.44 |  |  | 259
1986-05-31 | 3234.57 |  |  | 259
1986-05-30 | 3234.61 |  |  | 258
1986-05-29 | 3234.65 |  |  | 257
1986-05-28 | 3234.75 |  |  | 257
1986-05-27 | 3234.76 |  |  | 257
1986-05-26 | 3234.77 |  |  | 257
1986-05-25 | 3234.76 |  |  | 257
1986-05-24 | 3234.73 |  |  | 256
1986-05-23 | 3234.69 |  |  | 254
1986-05-22 | 3234.65 |  |  | 254
1986-05-21 | 3234.64 |  |  | 254
1986-05-20 | 3234.65 |  |  | 276
1986-05-19 | 3234.72 |  |  | 314
1986-05-18 | 3234.8 |  |  | 313
1986-05-17 | 3234.89 |  |  | 313
1986-05-16 | 3234.93 |  |  | 315
1986-05-15 | 3235.03 |  |  | 318
1986-05-14 | 3235.04 |  |  | 320
1986-05-13 | 3235.04 |  |  | 321
1986-05-12 | 3235.04 |  |  | 321
1986-05-11 | 3235 |  |  | 321
1986-05-10 | 3235 |  |  | 321
1986-05-09 | 3235 |  |  | 321
1986-05-08 | 3235 |  |  | 269
1986-05-07 | 3234.91 |  |  | 211
1986-05-06 | 3234.9 |  |  | 358
1986-05-05 | 3234.9 |  |  | 358
1986-05-04 | 3234.9 |  |  | 357
1986-05-03 | 3234.9 |  |  | 356
1986-05-02 | 3234.9 |  |  | 377
1986-05-01 | 3234.95 |  |  | 419
1986-04-30 | 3234.96 |  |  | 421
1986-04-29 | 3234.96 |  |  | 423
1986-04-28 | 3234.96 |  |  | 443
1986-04-27 | 3234.98 |  |  | 485
1986-04-26 | 3234.98 |  |  | 486
1986-04-25 | 3234.98 |  |  | 489
1986-04-24 | 3234.93 |  |  | 489
1986-04-23 | 3234.87 |  |  | 485
1986-04-22 | 3234.86 |  |  | 485
1986-04-21 | 3234.86 |  |  | 484
1986-04-20 | 3234.79 |  |  | 483
1986-04-19 | 3234.76 |  |  | 484
1986-04-18 | 3234.72 |  |  | 634
1986-04-17 | 3234.89 |  |  | 871
1986-04-16 | 3235.09 |  |  | 875
1986-04-15 | 3235.2 |  |  | 883
1986-04-14 | 3235.26 |  |  | 934
1986-04-13 | 3235.36 |  |  | 1020
1986-04-12 | 3235.37 |  |  | 1020
1986-04-11 | 3235.37 |  |  | 1020
1986-04-10 | 3235.33 |  |  | 1020
1986-04-09 | 3235.27 |  |  | 1010
1986-04-08 | 3235.23 |  |  | 1050
1986-04-07 | 3235.24 |  |  | 1230
1986-04-06 | 3235.4 |  |  | 1430
1986-04-05 | 3235.65 |  |  | 1450
1986-04-04 | 3235.87 |  |  | 1560
1986-04-03 | 3236.14 |  |  | 1750
1986-04-02 | 3236.54 |  |  | 1800
1986-04-01 | 3236.83 |  |  | 1830
1986-03-31 | 3236.96 |  |  | 1850
1986-03-30 | 3236.95 |  |  | 1840
1986-03-29 | 3236.84 |  |  | 1810
1986-03-28 | 3236.59 |  |  | 1770
1986-03-27 | 3236.38 |  |  | 1760
1986-03-26 | 3236.32 |  |  | 1760
1986-03-25 | 3236.26 |  |  | 1750
1986-03-24 | 3236.11 |  |  | 1640
1986-03-23 | 3235.8 |  |  | 1520
1986-03-22 | 3235.68 |  |  | 1360
1986-03-21 | 3235.42 |  |  | 1010
1986-03-20 | 3234.97 |  |  | 993
1986-03-19 | 3234.73 |  |  | 989
1986-03-18 | 3234.59 |  |  | 989
1986-03-17 | 3234.39 |  |  | 1090
1986-03-16 | 3234.21 |  |  | 1280
1986-03-15 | 3234.11 |  |  | 1460
1986-03-14 | 3234.02 |  |  | 1740
1986-03-13 | 3233.95 |  |  | 1830
1986-03-12 | 3233.85 |  |  | 2150
1986-03-11 | 3233.68 |  |  | 2720
1986-03-10 | 3233.58 |  |  | 2990
1986-03-09 | 3233.48 |  |  | 3150
1986-03-08 | 3232.62 |  |  | 2980
1986-03-07 | 3230.26 |  |  | 2370
1986-03-06 | 3228.51 |  |  | 2360
1986-03-05 | 3228.18 |  |  | 2360
1986-03-04 | 3228.01 |  |  | 2180
1986-03-03 | 3227.65 |  |  | 2350
1986-03-02 | 3227.28 |  |  | 2340
1986-03-01 | 3226.61 |  |  | 2340
1986-02-28 | 3225.83 |  |  | 2330
1986-02-27 | 3224.92 |  |  | 2330
1986-02-26 | 3223.86 |  |  | 2100
1986-02-25 | 3222.58 |  |  | 1770
1986-02-24 | 3220.63 |  |  | 1430
1986-02-23 | 3217.27 |  |  | 931
1986-02-22 | 3212.91 |  |  | 918
1986-02-21 | 3211.55 |  |  | 1160
1986-02-20 | 3211.79 |  |  | 1780
1986-02-19 | 3212.22 |  |  | 2140
1986-02-18 | 3212.52 |  |  | 1490
1986-02-17 | 3211.99 |  |  | 433
1986-02-16 | 3210.78 |  |  | 334
1986-02-15 | 3210.35 |  |  | 334
1986-02-14 | 3210.33 |  |  | 334
1986-02-13 | 3210.3 |  |  | 334
1986-02-12 | 3210.22 |  |  | 334
1986-02-11 | 3210.2 |  |  | 601
1986-02-10 | 3210.49 |  |  | 1210
1986-02-09 | 3211.24 |  |  | 1520
1986-02-08 | 3212.17 |  |  | 1520
1986-02-07 | 3213.04 |  |  | 1610
1986-02-06 | 3214.01 |  |  | 1760
1986-02-05 | 3214.82 |  |  | 1760
1986-02-04 | 3215.54 |  |  | 1730
1986-02-03 | 3216.13 |  |  | 1490
1986-02-02 | 3216.22 |  |  | 1230
1986-02-01 | 3216.11 |  |  | 1230
1986-01-31 | 3215.77 |  |  | 838
1986-01-30 | 3214.77 |  |  | 295
1986-01-29 | 3214.15 |  |  | 295
1986-01-28 | 3214.16 |  |  | 295
1986-01-27 | 3214.16 |  |  | 305
1986-01-26 | 3214.19 |  |  | 321
1986-01-25 | 3214.19 |  |  | 321
1986-01-24 | 3214.19 |  |  | 321
1986-01-23 | 3214.19 |  |  | 204
1986-01-22 | 3214.05 |  |  | 106
1986-01-21 | 3213.81 |  |  | 106
1986-01-20 | 3213.5 |  |  | 106
1986-01-19 | 3213.09 |  |  | 105
1986-01-18 | 3212.7 |  |  | 104
1986-01-17 | 3212.23 |  |  | 104
1986-01-16 | 3211.94 |  |  | 104
1986-01-15 | 3211.81 |  |  | 104
1986-01-14 | 3211.76 |  |  | 104
1986-01-13 | 3211.71 |  |  | 104
1986-01-12 | 3211.65 |  |  | 104
1986-01-11 | 3211.59 |  |  | 104
1986-01-10 | 3211.5 |  |  | 104
1986-01-09 | 3211.45 |  |  | 104
1986-01-08 | 3211.35 |  |  | 104
1986-01-07 | 3211.31 |  |  | 104
1986-01-06 | 3211.3 |  |  | 104
1986-01-05 | 3211.22 |  |  | 104
1986-01-04 | 3211.2 |  |  | 104
1986-01-03 | 3211.2 |  |  | 104
1986-01-02 | 3211.2 |  |  | 104
1986-01-01 | 3211.2 |  |  | 104
1985-12-31 | 3211.2 |  |  | 104
1985-12-30 | 3211.2 |  |  | 112
1985-12-29 | 3211.28 |  |  | 124
1985-12-28 | 3211.31 |  |  | 124
1985-12-27 | 3211.32 |  |  | 124
1985-12-26 | 3211.32 |  |  | 124
1985-12-25 | 3211.32 |  |  | 124
1985-12-24 | 3211.32 |  |  | 124
1985-12-23 | 3211.37 |  |  | 124
1985-12-22 | 3211.39 |  |  | 124
1985-12-21 | 3211.39 |  |  | 124
1985-12-20 | 3211.39 |  |  | 124
1985-12-19 | 3211.39 |  |  | 124
1985-12-18 | 3211.39 |  |  | 124
1985-12-17 | 3211.39 |  |  | 124
1985-12-16 | 3211.39 |  |  | 124
1985-12-15 | 3211.36 |  |  | 123
1985-12-14 | 3211.36 |  |  | 123
1985-12-13 | 3211.36 |  |  | 123
1985-12-12 | 3211.36 |  |  | 123
1985-12-11 | 3211.36 |  |  | 123
1985-12-10 | 3211.3 |  |  | 123
1985-12-09 | 3211.29 |  |  | 123
1985-12-08 | 3211.25 |  |  | 123
1985-12-07 | 3211.18 |  |  | 123
1985-12-06 | 3211.1 |  |  | 123
1985-12-05 | 3211.03 |  |  | 123
1985-12-04 | 3211.01 |  |  | 123
1985-12-03 | 3211.01 |  |  | 123
1985-12-02 | 3211.01 |  |  | 123
1985-12-01 | 3211.01 |  |  | 123
1985-11-30 | 3211.01 |  |  | 123
1985-11-29 | 3211.02 |  |  | 123
1985-11-28 | 3211.02 |  |  | 123
1985-11-27 | 3211.02 |  |  | 145
1985-11-26 | 3211.09 |  |  | 176
1985-11-25 | 3211.17 |  |  | 176
1985-11-24 | 3211.22 |  |  | 176
1985-11-23 | 3211.31 |  |  | 176
1985-11-22 | 3211.41 |  |  | 176
1985-11-21 | 3211.46 |  |  | 176
1985-11-20 | 3211.54 |  |  | 176
1985-11-19 | 3211.57 |  |  | 176
1985-11-18 | 3211.59 |  |  | 196
1985-11-17 | 3211.67 |  |  | 230
1985-11-16 | 3211.8 |  |  | 230
1985-11-15 | 3211.87 |  |  | 230
1985-11-14 | 3211.96 |  |  | 230
1985-11-13 | 3212.03 |  |  | 230
1985-11-12 | 3212.2 |  |  | 230
1985-11-11 | 3212.28 |  |  | 230
1985-11-10 | 3212.41 |  |  | 230
1985-11-09 | 3212.51 |  |  | 230
1985-11-08 | 3212.6 |  |  | 230
1985-11-07 | 3212.68 |  |  | 230
1985-11-06 | 3212.77 |  |  | 141
1985-11-05 | 3212.75 |  |  | 203
1985-11-04 | 3212.89 |  |  | 261
1985-11-03 | 3213.06 |  |  | 261
1985-11-02 | 3213.15 |  |  | 261
1985-11-01 | 3213.27 |  |  | 261
1985-10-31 | 3213.39 |  |  | 261
1985-10-30 | 3213.58 |  |  | 261
1985-10-29 | 3213.67 |  |  | 261
1985-10-28 | 3213.78 |  |  | 261
1985-10-27 | 3214 |  |  | 261
1985-10-26 | 3214.1 |  |  | 261
1985-10-25 | 3214.17 |  |  | 261
1985-10-24 | 3214.26 |  |  | 263
1985-10-23 | 3214.36 |  |  | 264
1985-10-22 | 3214.41 |  |  | 264
1985-10-21 | 3214.57 |  |  | 264
1985-10-20 | 3214.68 |  |  | 264
1985-10-19 | 3214.86 |  |  | 263
1985-10-18 | 3214.98 |  |  | 262
1985-10-17 | 3215.13 |  |  | 217
1985-10-16 | 3215.19 |  |  | 206
1985-10-15 | 3215.33 |  |  | 261
1985-10-14 | 3215.43 |  |  | 262
1985-10-13 | 3215.57 |  |  | 264
1985-10-12 | 3215.59 |  |  | 264
1985-10-11 | 3215.7 |  |  | 264
1985-10-10 | 3216.1 |  |  | 264
1985-10-09 | 3216.19 |  |  | 264
1985-10-08 | 3216.33 |  |  | 265
1985-10-07 | 3216.54 |  |  | 241
1985-10-06 | 3216.69 |  |  | 195
1985-10-05 | 3216.81 |  |  | 195
1985-10-04 | 3216.92 |  |  | 195
1985-10-03 | 3217.03 |  |  | 195
1985-10-02 | 3217.14 |  |  | 195
1985-10-01 | 3217.23 |  |  | 195
1985-09-30 | 3217.34 |  |  | 195
1985-09-29 | 3217.49 |  |  | 195
1985-09-28 | 3217.59 |  |  | 195
1985-09-27 | 3217.73 |  |  | 195
1985-09-26 | 3217.84 |  |  | 195
1985-09-25 | 3217.96 |  |  | 195
1985-09-24 | 3218.05 |  |  | 195
1985-09-23 | 3218.17 |  |  | 195
1985-09-22 | 3218.29 |  |  | 195
1985-09-21 | 3218.4 |  |  | 195
1985-09-20 | 3218.5 |  |  | 195
1985-09-19 | 3218.6 |  |  | 195
1985-09-18 | 3218.68 |  |  | 195
1985-09-17 | 3218.78 |  |  | 195
1985-09-16 | 3218.91 |  |  | 195
1985-09-15 | 3219 |  |  | 195
1985-09-14 | 3219.12 |  |  | 195
1985-09-13 | 3219.23 |  |  | 195
1985-09-12 | 3219.31 |  |  | 195
1985-09-11 | 3219.42 |  |  | 195
1985-09-10 | 3219.56 |  |  | 195
1985-09-09 | 3219.65 |  |  | 209
1985-09-08 | 3219.81 |  |  | 228
1985-09-07 | 3219.93 |  |  | 228
1985-09-06 | 3220.11 |  |  | 229
1985-09-05 | 3220.29 |  |  | 229
1985-09-04 | 3220.46 |  |  | 229
1985-09-03 | 3220.65 |  |  | 229
1985-09-02 | 3220.79 |  |  | 230
1985-09-01 | 3220.95 |  |  | 230
1985-08-31 | 3221.17 |  |  | 230
1985-08-30 | 3221.33 |  |  | 230
1985-08-29 | 3221.52 |  |  | 230
1985-08-28 | 3221.69 |  |  | 230
1985-08-27 | 3221.89 |  |  | 230
1985-08-26 | 3222.05 |  |  | 230
1985-08-25 | 3222.23 |  |  | 230
1985-08-24 | 3222.37 |  |  | 230
1985-08-23 | 3222.53 |  |  | 230
1985-08-22 | 3222.68 |  |  | 230
1985-08-21 | 3222.84 |  |  | 230
1985-08-20 | 3223.01 |  |  | 230
1985-08-19 | 3223.21 |  |  | 230
1985-08-18 | 3223.37 |  |  | 230
1985-08-17 | 3223.58 |  |  | 230
1985-08-16 | 3223.72 |  |  | 230
1985-08-15 | 3223.89 |  |  | 230
1985-08-14 | 3224.06 |  |  | 231
1985-08-13 | 3224.21 |  |  | 231
1985-08-12 | 3224.36 |  |  | 232
1985-08-11 | 3224.52 |  |  | 232
1985-08-10 | 3224.65 |  |  | 232
1985-08-09 | 3224.81 |  |  | 232
1985-08-08 | 3224.97 |  |  | 232
1985-08-07 | 3225.16 |  |  | 232
1985-08-06 | 3225.32 |  |  | 232
1985-08-05 | 3225.49 |  |  | 232
1985-08-04 | 3225.63 |  |  | 232
1985-08-03 | 3225.83 |  |  | 232
1985-08-02 | 3225.95 |  |  | 232
1985-08-01 | 3226.11 |  |  | 232
1985-07-31 | 3226.26 |  |  | 232
1985-07-30 | 3226.41 |  |  | 232
1985-07-29 | 3226.56 |  |  | 232
1985-07-28 | 3226.76 |  |  | 232
1985-07-27 | 3226.93 |  |  | 232
1985-07-26 | 3227.08 |  |  | 232
1985-07-25 | 3227.25 |  |  | 232
1985-07-24 | 3227.39 |  |  | 232
1985-07-23 | 3227.55 |  |  | 232
1985-07-22 | 3227.72 |  |  | 245
1985-07-21 | 3227.89 |  |  | 264
1985-07-20 | 3228.11 |  |  | 264
1985-07-19 | 3228.24 |  |  | 264
1985-07-18 | 3228.45 |  |  | 266
1985-07-17 | 3228.59 |  |  | 241
1985-07-16 | 3228.76 |  |  | 201
1985-07-15 | 3228.88 |  |  | 218
1985-07-14 | 3229.08 |  |  | 231
1985-07-13 | 3229.22 |  |  | 232
1985-07-12 | 3229.35 |  |  | 232
1985-07-11 | 3229.54 |  |  | 231
1985-07-10 | 3229.67 |  |  | 231
1985-07-09 | 3229.83 |  |  | 232
1985-07-08 | 3229.97 |  |  | 244
1985-07-07 | 3230.1 |  |  | 264
1985-07-06 | 3230.29 |  |  | 264
1985-07-05 | 3230.42 |  |  | 264
1985-07-04 | 3230.61 |  |  | 264
1985-07-03 | 3230.75 |  |  | 264
1985-07-02 | 3230.93 |  |  | 264
1985-07-01 | 3231.05 |  |  | 300
1985-06-30 | 3231.21 |  |  | 329
1985-06-29 | 3231.42 |  |  | 329
1985-06-28 | 3231.64 |  |  | 331
1985-06-27 | 3231.83 |  |  | 331
1985-06-26 | 3232.01 |  |  | 331
1985-06-25 | 3232.19 |  |  | 331
1985-06-24 | 3232.35 |  |  | 343
1985-06-23 | 3232.58 |  |  | 364
1985-06-22 | 3232.81 |  |  | 364
1985-06-21 | 3233.06 |  |  | 364
1985-06-20 | 3233.23 |  |  | 364
1985-06-19 | 3233.49 |  |  | 364
1985-06-18 | 3233.67 |  |  | 364
1985-06-17 | 3233.88 |  |  | 341
1985-06-16 | 3234.02 |  |  | 295
1985-06-15 | 3234.14 |  |  | 293
1985-06-14 | 3234.29 |  |  | 310
1985-06-13 | 3234.4 |  |  | 310
1985-06-12 | 3234.57 |  |  | 310
1985-06-11 | 3234.66 |  |  | 310
1985-06-10 | 3234.73 |  |  | 310
1985-06-09 | 3234.83 |  |  | 312
1985-06-08 | 3234.91 |  |  | 313
1985-06-07 | 3234.99 |  |  | 316
1985-06-06 | 3235.06 |  |  | 319
1985-06-05 | 3235.13 |  |  | 322
1985-06-04 | 3235.2 |  |  | 325
1985-06-03 | 3235.24 |  |  | 329
1985-06-02 | 3235.25 |  |  | 330
1985-06-01 | 3235.25 |  |  | 331
1985-05-31 | 3235.25 |  |  | 330
1985-05-30 | 3235.25 |  |  | 328
1985-05-29 | 3235.25 |  |  | 328
1985-05-28 | 3235.26 |  |  | 329
1985-05-27 | 3235.35 |  |  | 337
1985-05-26 | 3235.45 |  |  | 344
1985-05-25 | 3235.6 |  |  | 354
1985-05-24 | 3235.71 |  |  | 365
1985-05-23 | 3235.82 |  |  | 344
1985-05-22 | 3235.92 |  |  | 311
1985-05-21 | 3235.98 |  |  | 317
1985-05-20 | 3235.99 |  |  | 322
1985-05-19 | 3236.09 |  |  | 327
1985-05-18 | 3236.13 |  |  | 332
1985-05-17 | 3236.13 |  |  | 336
1985-05-16 | 3236.14 |  |  | 340
1985-05-15 | 3236.24 |  |  | 343
1985-05-14 | 3236.26 |  |  | 348
1985-05-13 | 3236.27 |  |  | 354
1985-05-12 | 3236.28 |  |  | 356
1985-05-11 | 3236.28 |  |  | 357
1985-05-10 | 3236.28 |  |  | 376
1985-05-09 | 3236.31 |  |  | 411
1985-05-08 | 3236.31 |  |  | 434
1985-05-07 | 3236.28 |  |  | 478
1985-05-06 | 3236.28 |  |  | 502
1985-05-05 | 3236.18 |  |  | 533
1985-05-04 | 3236.17 |  |  | 527
1985-05-03 | 3236.16 |  |  | 518
1985-05-02 | 3236.09 |  |  | 510
1985-05-01 | 3235.97 |  |  | 548
1985-04-30 | 3235.97 |  |  | 635
1985-04-29 | 3235.97 |  |  | 695
1985-04-28 | 3236.06 |  |  | 832
1985-04-27 | 3236.11 |  |  | 840
1985-04-26 | 3236.11 |  |  | 867
1985-04-25 | 3236.14 |  |  | 635
1985-04-24 | 3235.87 |  |  | 488
1985-04-23 | 3235.64 |  |  | 934
1985-04-22 | 3235.52 |  |  | 984
1985-04-21 | 3235.39 |  |  | 1090
1985-04-20 | 3235.34 |  |  | 1080
1985-04-19 | 3235.13 |  |  | 1160
1985-04-18 | 3234.89 |  |  | 1460
1985-04-17 | 3234.71 |  |  | 1760
1985-04-16 | 3234.55 |  |  | 1910
1985-04-15 | 3234.32 |  |  | 2100
1985-04-14 | 3234.11 |  |  | 2440
1985-04-13 | 3234.05 |  |  | 2440
1985-04-12 | 3233.91 |  |  | 2610
1985-04-11 | 3233.71 |  |  | 2930
1985-04-10 | 3233.33 |  |  | 2920
1985-04-09 | 3232.78 |  |  | 2750
1985-04-08 | 3232 |  |  | 2140
1985-04-07 | 3230.39 |  |  | 1930
1985-04-06 | 3228.67 |  |  | 1640
1985-04-05 | 3226.76 |  |  | 1630
1985-04-04 | 3224.82 |  |  | 1400
1985-04-03 | 3222.87 |  |  | 1100
1985-04-02 | 3220.8 |  |  | 878
1985-04-01 | 3218.94 |  |  | 460
1985-03-31 | 3217.63 |  |  | 459
1985-03-30 | 3216.95 |  |  | 457
1985-03-29 | 3216.52 |  |  | 457
1985-03-28 | 3216.06 |  |  | 457
1985-03-27 | 3215.58 |  |  | 454
1985-03-26 | 3215.05 |  |  | 453
1985-03-25 | 3214.29 |  |  | 695
1985-03-24 | 3213.26 |  |  | 1140
1985-03-23 | 3212.51 |  |  | 1140
1985-03-22 | 3212.15 |  |  | 1300
1985-03-21 | 3211.49 |  |  | 1600
1985-03-20 | 3210.35 |  |  | 1590
1985-03-19 | 3209.47 |  |  | 1420
1985-03-18 | 3208.48 |  |  | 854
1985-03-17 | 3207.16 |  |  | 438
1985-03-16 | 3205.76 |  |  | 437
1985-03-15 | 3204.79 |  |  | 436
1985-03-14 | 3204.2 |  |  | 433
1985-03-13 | 3203.8 |  |  | 433
1985-03-12 | 3203.53 |  |  | 433
1985-03-11 | 3203.3 |  |  | 433
1985-03-10 | 3203.24 |  |  | 433
1985-03-09 | 3203.24 |  |  | 433
1985-03-08 | 3203.24 |  |  | 433
1985-03-07 | 3203.24 |  |  | 431
1985-03-06 | 3203.18 |  |  | 431
1985-03-05 | 3203.17 |  |  | 430
1985-03-04 | 3203.17 |  |  | 430
1985-03-03 | 3203.04 |  |  | 430
1985-03-02 | 3202.98 |  |  | 430
1985-03-01 | 3202.83 |  |  | 430
1985-02-28 | 3202.6 |  |  | 430
1985-02-27 | 3202.5 |  |  | 430
1985-02-26 | 3202.37 |  |  | 427
1985-02-25 | 3202.18 |  |  | 427
1985-02-24 | 3201.86 |  |  | 427
1985-02-23 | 3201.69 |  |  | 427
1985-02-22 | 3201.64 |  |  | 427
1985-02-21 | 3201.7 |  |  | 427
1985-02-20 | 3201.81 |  |  | 427
1985-02-19 | 3201.92 |  |  | 427
1985-02-18 | 3202.04 |  |  | 458
1985-02-17 | 3202.18 |  |  | 517
1985-02-16 | 3202.32 |  |  | 518
1985-02-15 | 3202.4 |  |  | 518
1985-02-14 | 3202.5 |  |  | 518
1985-02-13 | 3202.71 |  |  | 518
1985-02-12 | 3202.87 |  |  | 518
1985-02-11 | 3203.06 |  |  | 518
1985-02-10 | 3203.35 |  |  | 518
1985-02-09 | 3203.66 |  |  | 518
1985-02-08 | 3203.89 |  |  | 518
1985-02-07 | 3204.12 |  |  | 519
1985-02-06 | 3204.37 |  |  | 519
1985-02-05 | 3204.69 |  |  | 521
1985-02-04 | 3205.03 |  |  | 522
1985-02-03 | 3205.36 |  |  | 522
1985-02-02 | 3205.61 |  |  | 522
1985-02-01 | 3205.91 |  |  | 449
1985-01-31 | 3206.13 |  |  | 323
1985-01-30 | 3206.21 |  |  | 323
1985-01-29 | 3206.28 |  |  | 323
1985-01-28 | 3206.34 |  |  | 344
1985-01-27 | 3206.46 |  |  | 381
1985-01-26 | 3206.64 |  |  | 381
1985-01-25 | 3206.8 |  |  | 381
1985-01-24 | 3206.87 |  |  | 381
1985-01-23 | 3206.97 |  |  | 381
1985-01-22 | 3207.09 |  |  | 381
1985-01-21 | 3207.16 |  |  | 381
1985-01-20 | 3207.26 |  |  | 381
1985-01-19 | 3207.37 |  |  | 381
1985-01-18 | 3207.51 |  |  | 382
1985-01-17 | 3207.65 |  |  | 383
1985-01-16 | 3207.78 |  |  | 384
1985-01-15 | 3207.89 |  |  | 339
1985-01-14 | 3207.97 |  |  | 261
1985-01-13 | 3207.99 |  |  | 261
1985-01-12 | 3207.99 |  |  | 261
1985-01-11 | 3207.94 |  |  | 261
1985-01-10 | 3207.92 |  |  | 261
1985-01-09 | 3207.9 |  |  | 261
1985-01-08 | 3207.82 |  |  | 261
1985-01-07 | 3207.8 |  |  | 261
1985-01-06 | 3207.71 |  |  | 261
1985-01-05 | 3207.7 |  |  | 261
1985-01-04 | 3207.69 |  |  | 261
1985-01-03 | 3207.69 |  |  | 261
1985-01-02 | 3207.69 |  |  | 261
1985-01-01 | 3207.68 |  |  | 261
1984-12-31 | 3207.67 |  |  | 261
1984-12-30 | 3207.57 |  |  | 261
1984-12-29 | 3207.45 |  |  | 261
1984-12-28 | 3207.32 |  |  | 261
1984-12-27 | 3207.21 |  |  | 261
1984-12-26 | 3207.09 |  |  | 261
1984-12-25 | 3206.98 |  |  | 259
1984-12-24 | 3206.89 |  |  | 259
1984-12-23 | 3206.72 |  |  | 259
1984-12-22 | 3206.55 |  |  | 259
1984-12-21 | 3206.44 |  |  | 293
1984-12-20 | 3206.53 |  |  | 318
1984-12-19 | 3206.61 |  |  | 360
1984-12-18 | 3206.68 |  |  | 430
1984-12-17 | 3206.68 |  |  | 577
1984-12-16 | 3206.86 |  |  | 829
1984-12-15 | 3207.26 |  |  | 829
1984-12-14 | 3207.57 |  |  | 831
1984-12-13 | 3207.91 |  |  | 963
1984-12-12 | 3208.27 |  |  | 1180
1984-12-11 | 3208.86 |  |  | 1320
1984-12-10 | 3209.58 |  |  | 1320
1984-12-09 | 3210.33 |  |  | 1330
1984-12-08 | 3211.16 |  |  | 1330
1984-12-07 | 3212.08 |  |  | 1340
1984-12-06 | 3212.98 |  |  | 1240
1984-12-05 | 3213.83 |  |  | 1350
1984-12-04 | 3214.68 |  |  | 1350
1984-12-03 | 3215.46 |  |  | 996
1984-12-02 | 3216 |  |  | 589
1984-12-01 | 3216.21 |  |  | 593
1984-11-30 | 3216.24 |  |  | 219
1984-11-29 | 3215.93 |  |  | 14
1984-11-28 | 3215.47 |  |  | 11
1984-11-27 | 3214.96 |  |  | 12
1984-11-26 | 3214.56 |  |  | 11
1984-11-25 | 3214.09 |  |  | 11
1984-11-24 | 3213.44 |  |  | 11
1984-11-23 | 3212.98 |  |  | 11
1984-11-22 | 3212.46 |  |  | 11
1984-11-21 | 3211.72 |  |  | 11
1984-11-20 | 3210.86 |  |  | 11
1984-11-19 | 3210.24 |  |  | 11
1984-11-18 | 3209.35 |  |  | 13
1984-11-17 | 3208.65 |  |  | 20
1984-11-16 | 3207.86 |  |  | 16
1984-11-15 | 3206.87 |  |  | 507
1984-11-14 | 3205.74 |  |  | 1630
1984-11-13 | 3204.59 |  |  | 1780
1984-11-12 | 3202.93 |  |  | 1900
1984-11-11 | 3202.03 |  |  | 1960
1984-11-10 | 3203.44 |  |  | 1970
1984-11-09 | 3205.05 |  |  | 1980
1984-11-08 | 3206.64 |  |  | 2000
1984-11-07 | 3208.2 |  |  | 2010
1984-11-06 | 3209.78 |  |  | 1990
1984-11-05 | 3211.34 |  |  | 1610
1984-11-04 | 3212.51 |  |  | 1190
1984-11-03 | 3213.02 |  |  | 1190
1984-11-02 | 3213.36 |  |  | 966
1984-11-01 | 3213.99 |  |  | 657
1984-10-31 | 3214.36 |  |  | 304
1984-10-30 | 3214.28 |  |  | 225
1984-10-29 | 3214.4 |  |  | 363
1984-10-28 | 3214.49 |  |  | 364
1984-10-27 | 3214.58 |  |  | 364
1984-10-26 | 3214.62 |  |  | 340
1984-10-25 | 3214.8 |  |  | 373
1984-10-24 | 3215.07 |  |  | 373
1984-10-23 | 3215.14 |  |  | 373
1984-10-22 | 3215.22 |  |  | 373
1984-10-21 | 3215.28 |  |  | 373
1984-10-20 | 3215.4 |  |  | 373
1984-10-19 | 3215.49 |  |  | 325
1984-10-18 | 3215.59 |  |  | 293
1984-10-17 | 3215.72 |  |  | 293
1984-10-16 | 3215.81 |  |  | 293
1984-10-15 | 3215.9 |  |  | 293
1984-10-14 | 3216.03 |  |  | 293
1984-10-13 | 3216.14 |  |  | 293
1984-10-12 | 3216.27 |  |  | 293
1984-10-11 | 3216.45 |  |  | 293
1984-10-10 | 3216.62 |  |  | 293
1984-10-09 | 3216.78 |  |  | 290
1984-10-08 | 3216.95 |  |  | 291
1984-10-07 | 3217.12 |  |  | 293
1984-10-06 | 3217.26 |  |  | 290
1984-10-05 | 3217.45 |  |  | 290
1984-10-04 | 3217.59 |  |  | 290
1984-10-03 | 3217.77 |  |  | 290
1984-10-02 | 3217.94 |  |  | 290
1984-10-01 | 3218.07 |  |  | 290
1984-09-30 | 3218.24 |  |  | 288
1984-09-29 | 3218.45 |  |  | 288
1984-09-28 | 3218.6 |  |  | 288
1984-09-27 | 3218.75 |  |  | 286
1984-09-26 | 3218.94 |  |  | 285
1984-09-25 | 3219.1 |  |  | 285
1984-09-24 | 3219.24 |  |  | 287
1984-09-23 | 3219.39 |  |  | 288
1984-09-22 | 3219.56 |  |  | 288
1984-09-21 | 3219.77 |  |  | 288
1984-09-20 | 3219.98 |  |  | 286
1984-09-19 | 3220.18 |  |  | 285
1984-09-18 | 3220.35 |  |  | 285
1984-09-17 | 3220.51 |  |  | 285
1984-09-16 | 3220.69 |  |  | 285
1984-09-15 | 3220.85 |  |  | 285
1984-09-14 | 3220.98 |  |  | 285
1984-09-13 | 3221.23 |  |  | 283
1984-09-12 | 3221.35 |  |  | 283
1984-09-11 | 3221.54 |  |  | 283
1984-09-10 | 3221.8 |  |  | 262
1984-09-09 | 3221.94 |  |  | 228
1984-09-08 | 3222.09 |  |  | 228
1984-09-07 | 3222.2 |  |  | 228
1984-09-06 | 3222.31 |  |  | 226
1984-09-05 | 3222.44 |  |  | 226
1984-09-04 | 3222.59 |  |  | 226
1984-09-03 | 3222.7 |  |  | 226
1984-09-02 | 3222.82 |  |  | 226
1984-09-01 | 3222.82 |  |  | 226
1984-08-31 | 3222.82 |  |  | 227
1984-08-30 | 3222.9 |  |  | 226
1984-08-29 | 3222.95 |  |  | 226
1984-08-28 | 3223.16 |  |  | 226
1984-08-27 | 3223.34 |  |  | 226
1984-08-26 | 3223.49 |  |  | 226
1984-08-25 | 3223.67 |  |  | 226
1984-08-24 | 3223.81 |  |  | 225
1984-08-23 | 3224 |  |  | 224
1984-08-22 | 3224.21 |  |  | 225
1984-08-21 | 3224.35 |  |  | 226
1984-08-20 | 3224.56 |  |  | 237
1984-08-19 | 3224.77 |  |  | 254
1984-08-18 | 3224.87 |  |  | 254
1984-08-17 | 3225.14 |  |  | 252
1984-08-16 | 3225.28 |  |  | 252
1984-08-15 | 3225.47 |  |  | 252
1984-08-14 | 3225.6 |  |  | 252
1984-08-13 | 3225.84 |  |  | 252
1984-08-12 | 3225.99 |  |  | 252
1984-08-11 | 3226.22 |  |  | 254
1984-08-10 | 3226.4 |  |  | 254
1984-08-09 | 3226.57 |  |  | 254
1984-08-08 | 3226.73 |  |  | 256
1984-08-07 | 3226.9 |  |  | 257
1984-08-06 | 3226.99 |  |  | 259
1984-08-05 | 3227.17 |  |  | 259
1984-08-04 | 3227.34 |  |  | 259
1984-08-03 | 3227.51 |  |  | 259
1984-08-02 | 3227.63 |  |  | 259
1984-08-01 | 3227.84 |  |  | 261
1984-07-31 | 3227.97 |  |  | 261
1984-07-30 | 3228.1 |  |  | 261
1984-07-29 | 3228.2 |  |  | 262
1984-07-28 | 3228.36 |  |  | 263
1984-07-27 | 3228.53 |  |  | 266
1984-07-26 | 3228.68 |  |  | 266
1984-07-25 | 3228.83 |  |  | 266
1984-07-24 | 3228.96 |  |  | 293
1984-07-23 | 3229.11 |  |  | 338
1984-07-22 | 3229.27 |  |  | 339
1984-07-21 | 3229.5 |  |  | 339
1984-07-20 | 3229.71 |  |  | 339
1984-07-19 | 3229.97 |  |  | 339
1984-07-18 | 3230.2 |  |  | 305
1984-07-17 | 3230.35 |  |  | 241
1984-07-16 | 3230.43 |  |  | 240
1984-07-15 | 3230.58 |  |  | 239
1984-07-14 | 3230.66 |  |  | 239
1984-07-13 | 3230.71 |  |  | 240
1984-07-12 | 3230.89 |  |  | 241
1984-07-11 | 3230.95 |  |  | 241
1984-07-10 | 3231.05 |  |  | 241
1984-07-09 | 3231.1 |  |  | 241
1984-07-08 | 3231.2 |  |  | 242
1984-07-07 | 3231.3 |  |  | 242
1984-07-06 | 3231.37 |  |  | 243
1984-07-05 | 3231.47 |  |  | 243
1984-07-04 | 3231.51 |  |  | 269
1984-07-03 | 3231.64 |  |  | 315
1984-07-02 | 3231.71 |  |  | 315
1984-07-01 | 3231.79 |  |  | 317
1984-06-30 | 3231.85 |  |  | 318
1984-06-29 | 3231.93 |  |  | 376
1984-06-28 | 3232.09 |  |  | 474
1984-06-27 | 3232.2 |  |  | 580
1984-06-26 | 3232.35 |  |  | 774
1984-06-25 | 3232.67 |  |  | 774
1984-06-24 | 3232.95 |  |  | 774
1984-06-23 | 3233.15 |  |  | 774
1984-06-22 | 3233.32 |  |  | 774
1984-06-21 | 3233.47 |  |  | 775
1984-06-20 | 3233.72 |  |  | 776
1984-06-19 | 3233.96 |  |  | 776
1984-06-18 | 3234.14 |  |  | 775
1984-06-17 | 3234.31 |  |  | 775
1984-06-16 | 3234.49 |  |  | 775
1984-06-15 | 3234.62 |  |  | 774
1984-06-14 | 3234.66 |  |  | 774
1984-06-13 | 3234.66 |  |  | 774
1984-06-12 | 3234.66 |  |  | 774
1984-06-11 | 3234.66 |  |  | 774
1984-06-10 | 3234.58 |  |  | 774
1984-06-09 | 3234.54 |  |  | 773
1984-06-08 | 3234.47 |  |  | 770
1984-06-07 | 3234.37 |  |  | 733
1984-06-06 | 3234.25 |  |  | 625
1984-06-05 | 3234.14 |  |  | 511
1984-06-04 | 3233.8 |  |  | 511
1984-06-03 | 3233.66 |  |  | 511
1984-06-02 | 3233.53 |  |  | 510
1984-06-01 | 3233.38 |  |  | 507
1984-05-31 | 3233.13 |  |  | 433
1984-05-30 | 3232.79 |  |  | 988
1984-05-29 | 3233 |  |  | 1300
1984-05-28 | 3233.13 |  |  | 1300
1984-05-27 | 3233.22 |  |  | 1300
1984-05-26 | 3233.24 |  |  | 1300
1984-05-25 | 3233.24 |  |  | 1300
1984-05-24 | 3233.25 |  |  | 1300
1984-05-23 | 3233.21 |  |  | 1420
1984-05-22 | 3233.43 |  |  | 1770
1984-05-21 | 3233.6 |  |  | 1930
1984-05-20 | 3233.84 |  |  | 2250
1984-05-19 | 3234.23 |  |  | 2250
1984-05-18 | 3234.67 |  |  | 2250
1984-05-17 | 3235.11 |  |  | 2270
1984-05-16 | 3235.48 |  |  | 2300
1984-05-15 | 3235.68 |  |  | 2320
1984-05-14 | 3235.67 |  |  | 2230
1984-05-13 | 3235.4 |  |  | 2040
1984-05-12 | 3235.14 |  |  | 2010
1984-05-11 | 3234.89 |  |  | 2000
1984-05-10 | 3234.87 |  |  | 2000
1984-05-09 | 3234.87 |  |  | 2000
1984-05-08 | 3234.89 |  |  | 2240
1984-05-07 | 3235.2 |  |  | 2470
1984-05-06 | 3235.66 |  |  | 2510
1984-05-05 | 3236.06 |  |  | 2560
1984-05-04 | 3236.41 |  |  | 2800
1984-05-03 | 3236.77 |  |  | 3190
1984-05-02 | 3237.19 |  |  | 3150
1984-05-01 | 3237.37 |  |  | 2940
1984-04-30 | 3238.07 |  |  | 2950
1984-04-29 | 3238.93 |  |  | 2810
1984-04-28 | 3239.66 |  |  | 2870
1984-04-27 | 3240.43 |  |  | 2950
1984-04-26 | 3241.1 |  |  | 2970
1984-04-25 | 3241.63 |  |  | 3020
1984-04-24 | 3242.06 |  |  | 3060
1984-04-23 | 3242.2 |  |  | 3040
1984-04-22 | 3242.35 |  |  | 3010
1984-04-21 | 3242.5 |  |  | 3020
1984-04-20 | 3242.7 |  |  | 3030
1984-04-19 | 3242.51 |  |  | 3030
1984-04-18 | 3242.08 |  |  | 3010
1984-04-17 | 3241.38 |  |  | 2980
1984-04-16 | 3240.43 |  |  | 3070
1984-04-15 | 3238.86 |  |  | 3050
1984-04-14 | 3238.35 |  |  | 3020
1984-04-13 | 3238.65 |  |  | 3060
1984-04-12 | 3239.07 |  |  | 3030
1984-04-11 | 3239.38 |  |  | 2980
1984-04-10 | 3239.36 |  |  | 3010
1984-04-09 | 3239.2 |  |  | 3100
1984-04-08 | 3238.7 |  |  | 3070
1984-04-07 | 3238.14 |  |  | 3060
1984-04-06 | 3237.93 |  |  | 3060
1984-04-05 | 3237.53 |  |  | 3070
1984-04-04 | 3237.26 |  |  | 2980
1984-04-03 | 3237.47 |  |  | 2940
1984-04-02 | 3237.88 |  |  | 2930
1984-04-01 | 3238.27 |  |  | 2850
1984-03-31 | 3238.53 |  |  | 2910
1984-03-30 | 3238.95 |  |  | 2980
1984-03-29 | 3239.45 |  |  | 2940
1984-03-28 | 3239.66 |  |  | 2870
1984-03-27 | 3239.6 |  |  | 2890
1984-03-26 | 3239.29 |  |  | 2880
1984-03-25 | 3238.95 |  |  | 2840
1984-03-24 | 3238.76 |  |  | 2850
1984-03-23 | 3238.46 |  |  | 2850
1984-03-22 | 3238.04 |  |  | 2790
1984-03-21 | 3237.31 |  |  | 2810
1984-03-20 | 3235.87 |  |  | 2770
1984-03-19 | 3235.68 |  |  | 2820
1984-03-18 | 3235.74 |  |  | 2900
1984-03-17 | 3235.73 |  |  | 2890
1984-03-16 | 3235.4 |  |  | 3020
1984-03-15 | 3234.63 |  |  | 3280
1984-03-14 | 3233.81 |  |  | 2700
1984-03-13 | 3232.59 |  |  | 1850
1984-03-12 | 3231.23 |  |  | 1260
1984-03-11 | 3229.59 |  |  | 696
1984-03-10 | 3226.93 |  |  | 689
1984-03-09 | 3226.93 |  |  | 573
1984-03-08 | 3221.14 |  |  | 369
1984-03-07 | 3221.14 |  |  | 367
1984-03-06 | 3221.14 |  |  | 365
1984-03-05 | 3218.45 |  |  | 364
1984-03-04 | 3217.69 |  |  | 363
1984-03-03 | 3216.88 |  |  | 361
1984-03-02 | 3215.91 |  |  | 360
1984-03-01 | 3214.73 |  |  | 358
1984-02-29 | 3214.18 |  |  | 358
1984-02-28 | 3213.91 |  |  | 358
1984-02-27 | 3213.69 |  |  | 358
1984-02-26 | 3213.53 |  |  | 356
1984-02-25 | 3213.34 |  |  | 356
1984-02-24 | 3212.98 |  |  | 431
1984-02-23 | 3212.81 |  |  | 561
1984-02-22 | 3212.66 |  |  | 701
1984-02-21 | 3212.78 |  |  | 1140
1984-02-20 | 3213 |  |  | 1430
1984-02-19 | 3213.5 |  |  | 1430
1984-02-18 | 3214.02 |  |  | 1430
1984-02-17 | 3214.46 |  |  | 1430
1984-02-16 | 3214.62 |  |  | 1160
1984-02-15 | 3214.26 |  |  | 657
1984-02-14 | 3213.27 |  |  | 517
1984-02-13 | 3211.51 |  |  | 323
1984-02-12 | 3210.67 |  |  | 323
1984-02-11 | 3210.46 |  |  | 323
1984-02-10 | 3210.34 |  |  | 323
1984-02-09 | 3210.25 |  |  | 323
1984-02-08 | 3210.13 |  |  | 323
1984-02-07 | 3210.04 |  |  | 323
1984-02-06 | 3209.93 |  |  | 386
1984-02-05 | 3209.98 |  |  | 496
1984-02-04 | 3210.05 |  |  | 496
1984-02-03 | 3210.12 |  |  | 496
1984-02-02 | 3210.16 |  |  | 744
1984-02-01 | 3210.46 |  |  | 937
1984-01-31 | 3210.86 |  |  | 937
1984-01-30 | 3211.24 |  |  | 979
1984-01-29 | 3211.58 |  |  | 1050
1984-01-28 | 3211.93 |  |  | 1050
1984-01-27 | 3212.27 |  |  | 890
1984-01-26 | 3212.32 |  |  | 486
1984-01-25 | 3212.15 |  |  | 300
1984-01-24 | 3211.96 |  |  | 300
1984-01-23 | 3211.96 |  |  | 228
1984-01-22 | 3211.79 |  |  | 148
1984-01-21 | 3211.7 |  |  | 148
1984-01-20 | 3211.59 |  |  | 148
1984-01-19 | 3211.54 |  |  | 115
1984-01-18 | 3211.38 |  |  | 64
1984-01-17 | 3211.2 |  |  | 64
1984-01-16 | 3210.98 |  |  | 64
1984-01-15 | 3210.79 |  |  | 64
1984-01-14 | 3210.58 |  |  | 64
1984-01-13 | 3210.26 |  |  | 64
1984-01-12 | 3209.94 |  |  | 236
1984-01-11 | 3209.87 |  |  | 835
1984-01-10 | 3210.23 |  |  | 1060
1984-01-09 | 3210.75 |  |  | 1070
1984-01-08 | 3211.22 |  |  | 1070
1984-01-07 | 3211.66 |  |  | 1070
1984-01-06 | 3212.1 |  |  | 1070
1984-01-05 | 3212.48 |  |  | 1070
1984-01-04 | 3212.86 |  |  | 1010
1984-01-03 | 3213.22 |  |  | 796
1984-01-02 | 3213.38 |  |  | 340
1984-01-01 | 3213.07 |  |  | 79
1983-12-31 | 3212.68 |  |  | 79
1983-12-30 | 3212.67 |  |  | 220
1983-12-29 | 3213.12 |  |  | 393
1983-12-28 | 3213.34 |  |  | 393
1983-12-27 | 3213.31 |  |  | 395
1983-12-26 | 3212.04 |  |  | 403
1983-12-25 | 3212.03 |  |  | 411
1983-12-24 | 3212.03 |  |  | 411
1983-12-23 | 3212.03 |  |  | 493
1983-12-22 | 3212.03 |  |  | 773
1983-12-21 | 3212.02 |  |  | 1050
1983-12-20 | 3212.72 |  |  | 1060
1983-12-19 | 3213.27 |  |  | 953
1983-12-18 | 3213.69 |  |  | 799
1983-12-17 | 3213.74 |  |  | 799
1983-12-16 | 3213.74 |  |  | 799
1983-12-15 | 3213.64 |  |  | 799
1983-12-14 | 3213.3 |  |  | 799
1983-12-13 | 3213.34 |  |  | 604
1983-12-12 | 3213.23 |  |  | 475
1983-12-11 | 3212.98 |  |  | 441
1983-12-10 | 3212.53 |  |  | 440
1983-12-09 | 3212.31 |  |  | 425
1983-12-08 | 3212.31 |  |  | 414
1983-12-07 | 3212.34 |  |  | 414
1983-12-06 | 3212.47 |  |  | 415
1983-12-05 | 3212.6 |  |  | 414
1983-12-04 | 3212.79 |  |  | 415
1983-12-03 | 3213.01 |  |  | 417
1983-12-02 | 3213.19 |  |  | 417
1983-12-01 | 3213.39 |  |  | 417
1983-11-30 | 3213.61 |  |  | 417
1983-11-29 | 3213.77 |  |  | 417
1983-11-28 | 3213.97 |  |  | 417
1983-11-27 | 3214.13 |  |  | 417
1983-11-26 | 3214.27 |  |  | 417
1983-11-25 | 3214.44 |  |  | 417
1983-11-24 | 3214.61 |  |  | 417
1983-11-23 | 3214.86 |  |  | 188
1983-11-22 | 3214.74 |  |  | 11
1983-11-21 | 3214.59 |  |  | 11
1983-11-20 | 3214.39 |  |  | 11
1983-11-19 | 3214.17 |  |  | 11
1983-11-18 | 3213.91 |  |  | 11
1983-11-17 | 3213.56 |  |  | 11
1983-11-16 | 3213.26 |  |  | 11
1983-11-15 | 3213.12 |  |  | 11
1983-11-14 | 3212.96 |  |  | 11
1983-11-13 | 3212.83 |  |  | 11
1983-11-12 | 3212.71 |  |  | 11
1983-11-11 | 3212.56 |  |  | 11
1983-11-10 | 3212.46 |  |  | 11
1983-11-09 | 3212.32 |  |  | 20
1983-11-08 | 3212.22 |  |  | 88
1983-11-07 | 3212.25 |  |  | 288
1983-11-06 | 3212.42 |  |  | 367
1983-11-05 | 3212.63 |  |  | 367
1983-11-04 | 3212.86 |  |  | 367
1983-11-03 | 3213.11 |  |  | 367
1983-11-02 | 3213.33 |  |  | 367
1983-11-01 | 3213.59 |  |  | 367
1983-10-31 | 3213.71 |  |  | 368
1983-10-30 | 3213.96 |  |  | 370
1983-10-29 | 3214.18 |  |  | 370
1983-10-28 | 3214.39 |  |  | 370
1983-10-27 | 3214.67 |  |  | 370
1983-10-26 | 3214.89 |  |  | 370
1983-10-25 | 3215.12 |  |  | 370
1983-10-24 | 3215.33 |  |  | 354
1983-10-23 | 3215.52 |  |  | 373
1983-10-22 | 3215.76 |  |  | 373
1983-10-21 | 3215.98 |  |  | 373
1983-10-20 | 3216.21 |  |  | 340
1983-10-19 | 3216.45 |  |  | 300
1983-10-18 | 3216.64 |  |  | 300
1983-10-17 | 3216.78 |  |  | 300
1983-10-16 | 3216.95 |  |  | 300
1983-10-15 | 3217.13 |  |  | 300
1983-10-14 | 3217.29 |  |  | 300
1983-10-13 | 3217.5 |  |  | 288
1983-10-12 | 3217.66 |  |  | 273
1983-10-11 | 3217.8 |  |  | 273
1983-10-10 | 3217.95 |  |  | 273
1983-10-09 | 3218.09 |  |  | 273
1983-10-08 | 3218.24 |  |  | 273
1983-10-07 | 3218.41 |  |  | 273
1983-10-06 | 3218.57 |  |  | 267
1983-10-05 | 3218.75 |  |  | 261
1983-10-04 | 3218.91 |  |  | 261
1983-10-03 | 3219.07 |  |  | 261
1983-10-02 | 3219.24 |  |  | 261
1983-10-01 | 3219.41 |  |  | 261
1983-09-30 | 3219.6 |  |  | 239
1983-09-29 | 3219.71 |  |  | 224
1983-09-28 | 3219.83 |  |  | 224
1983-09-27 | 3220.01 |  |  | 224
1983-09-26 | 3220.17 |  |  | 224
1983-09-25 | 3220.32 |  |  | 224
1983-09-24 | 3220.45 |  |  | 224
1983-09-23 | 3220.59 |  |  | 224
1983-09-22 | 3220.71 |  |  | 224
1983-09-21 | 3220.84 |  |  | 224
1983-09-20 | 3220.97 |  |  | 224
1983-09-19 | 3221.17 |  |  | 224
1983-09-18 | 3221.3 |  |  | 223
1983-09-17 | 3221.48 |  |  | 223
1983-09-16 | 3221.63 |  |  | 222
1983-09-15 | 3221.82 |  |  | 222
1983-09-14 | 3221.97 |  |  | 222
1983-09-13 | 3222.12 |  |  | 222
1983-09-12 | 3222.26 |  |  | 222
1983-09-11 | 3222.4 |  |  | 222
1983-09-10 | 3222.53 |  |  | 223
1983-09-09 | 3222.68 |  |  | 222
1983-09-08 | 3222.81 |  |  | 223
1983-09-07 | 3222.98 |  |  | 224
1983-09-06 | 3223.18 |  |  | 224
1983-09-05 | 3223.32 |  |  | 224
1983-09-04 | 3223.4 |  |  | 224
1983-09-03 | 3223.59 |  |  | 224
1983-09-02 | 3223.69 |  |  | 245
1983-09-01 | 3223.86 |  |  | 260
1983-08-31 | 3224.06 |  |  | 260
1983-08-30 | 3224.23 |  |  | 260
1983-08-29 | 3224.39 |  |  | 260
1983-08-28 | 3224.56 |  |  | 260
1983-08-27 | 3224.71 |  |  | 260
1983-08-26 | 3224.87 |  |  | 260
1983-08-25 | 3225.09 |  |  | 246
1983-08-24 | 3225.22 |  |  | 233
1983-08-23 | 3225.38 |  |  | 233
1983-08-22 | 3225.54 |  |  | 233
1983-08-21 | 3225.69 |  |  | 235
1983-08-20 | 3225.87 |  |  | 235
1983-08-19 | 3226.04 |  |  | 235
1983-08-18 | 3226.21 |  |  | 235
1983-08-17 | 3226.36 |  |  | 235
1983-08-16 | 3226.52 |  |  | 230
1983-08-15 | 3226.66 |  |  | 225
1983-08-14 | 3226.81 |  |  | 224
1983-08-13 | 3226.93 |  |  | 224
1983-08-12 | 3227.05 |  |  | 226
1983-08-11 | 3227.21 |  |  | 225
1983-08-10 | 3227.35 |  |  | 225
1983-08-09 | 3227.52 |  |  | 225
1983-08-08 | 3227.65 |  |  | 224
1983-08-07 | 3227.8 |  |  | 224
1983-08-06 | 3227.96 |  |  | 224
1983-08-05 | 3228.1 |  |  | 224
1983-08-04 | 3228.21 |  |  | 262
1983-08-03 | 3228.42 |  |  | 286
1983-08-02 | 3228.6 |  |  | 286
1983-08-01 | 3228.8 |  |  | 298
1983-07-31 | 3229.02 |  |  | 309
1983-07-30 | 3229.17 |  |  | 309
1983-07-29 | 3229.31 |  |  | 309
1983-07-28 | 3229.52 |  |  | 309
1983-07-27 | 3229.69 |  |  | 309
1983-07-26 | 3229.89 |  |  | 309
1983-07-25 | 3230.06 |  |  | 309
1983-07-24 | 3230.3 |  |  | 310
1983-07-23 | 3230.49 |  |  | 310
1983-07-22 | 3230.65 |  |  | 310
1983-07-21 | 3230.8 |  |  | 311
1983-07-20 | 3231.15 |  |  | 311
1983-07-19 | 3231.31 |  |  | 311
1983-07-18 | 3231.46 |  |  | 311
1983-07-17 | 3231.62 |  |  | 312
1983-07-16 | 3231.74 |  |  | 314
1983-07-15 | 3231.89 |  |  | 314
1983-07-14 | 3232.05 |  |  | 314
1983-07-13 | 3232.25 |  |  | 380
1983-07-12 | 3233.64 |  |  | 417
1983-07-11 | 3233.64 |  |  | 417
1983-07-10 | 3233.64 |  |  | 417
1983-07-09 | 3233.64 |  |  | 417
1983-07-08 | 3233.64 |  |  | 417
1983-07-07 | 3233.64 |  |  | 417
1983-07-06 | 3233.64 |  |  | 350
1983-07-05 | 3233.7 |  |  | 286
1983-07-04 | 3233.77 |  |  | 286
1983-07-03 | 3233.77 |  |  | 286
1983-07-02 | 3233.78 |  |  | 286
1983-07-01 | 3233.8 |  |  | 286
1983-06-30 | 3233.8 |  |  | 286
1983-06-29 | 3233.9 |  |  | 286
1983-06-28 | 3233.93 |  |  | 286
1983-06-27 | 3234.02 |  |  | 286
1983-06-26 | 3234.06 |  |  | 285
1983-06-25 | 3234.15 |  |  | 285
1983-06-24 | 3234.2 |  |  | 284
1983-06-23 | 3234.29 |  |  | 285
1983-06-22 | 3234.38 |  |  | 284
1983-06-21 | 3234.42 |  |  | 323
1983-06-20 | 3234.53 |  |  | 372
1983-06-19 | 3234.66 |  |  | 372
1983-06-18 | 3234.79 |  |  | 372
1983-06-17 | 3234.9 |  |  | 372
1983-06-16 | 3235.01 |  |  | 372
1983-06-15 | 3235.06 |  |  | 372
1983-06-14 | 3235.14 |  |  | 374
1983-06-13 | 3235.19 |  |  | 375
1983-06-12 | 3235.19 |  |  | 375
1983-06-11 | 3235.19 |  |  | 375
1983-06-10 | 3235.21 |  |  | 441
1983-06-09 | 3235.32 |  |  | 524
1983-06-08 | 3235.41 |  |  | 528
1983-06-07 | 3235.41 |  |  | 362
1983-06-06 | 3235.34 |  |  | 704
1983-06-05 | 3235.54 |  |  | 1040
1983-06-04 | 3235.78 |  |  | 1060
1983-06-03 | 3235.97 |  |  | 1070
1983-06-02 | 3235.98 |  |  | 1070
1983-06-01 | 3235.85 |  |  | 1060
1983-05-31 | 3235.62 |  |  | 1130
1983-05-30 | 3235.62 |  |  | 1230
1983-05-29 | 3235.63 |  |  | 1230
1983-05-28 | 3235.62 |  |  | 1230
1983-05-27 | 3235.57 |  |  | 1220
1983-05-26 | 3235.43 |  |  | 1210
1983-05-25 | 3235.27 |  |  | 1320
1983-05-24 | 3235.05 |  |  | 1510
1983-05-23 | 3234.98 |  |  | 1330
1983-05-22 | 3234.75 |  |  | 1110
1983-05-21 | 3234.39 |  |  | 1100
1983-05-20 | 3234.02 |  |  | 1130
1983-05-19 | 3233.61 |  |  | 1180
1983-05-18 | 3233.61 |  |  | 1180
1983-05-17 | 3233.49 |  |  | 1180
1983-05-16 | 3233.39 |  |  | 1180
1983-05-15 | 3233.19 |  |  | 1180
1983-05-14 | 3233.01 |  |  | 1180
1983-05-13 | 3232.88 |  |  | 1300
1983-05-12 | 3232.88 |  |  | 1790
1983-05-11 | 3233.18 |  |  | 2530
1983-05-10 | 3233.82 |  |  | 3000
1983-05-09 | 3234.65 |  |  | 3010
1983-05-08 | 3235.42 |  |  | 3050
1983-05-07 | 3235.82 |  |  | 3080
1983-05-06 | 3236.03 |  |  | 2870
1983-05-05 | 3235.75 |  |  | 2470
1983-05-04 | 3235.6 |  |  | 2390
1983-05-03 | 3235.64 |  |  | 2240
1983-05-02 | 3235.63 |  |  | 2240
1983-05-01 | 3235.62 |  |  | 2230
1983-04-30 | 3235.57 |  |  | 2230
1983-04-29 | 3235.57 |  |  | 2230
1983-04-28 | 3235.78 |  |  | 2250
1983-04-27 | 3236.04 |  |  | 2280
1983-04-26 | 3236.35 |  |  | 2190
1983-04-25 | 3236.29 |  |  | 2020
1983-04-24 | 3236.15 |  |  | 2000
1983-04-23 | 3235.87 |  |  | 1960
1983-04-22 | 3235.48 |  |  | 1910
1983-04-21 | 3235 |  |  | 1900
1983-04-20 | 3234.39 |  |  | 1850
1983-04-19 | 3234.18 |  |  | 1390
1983-04-18 | 3233.85 |  |  | 883
1983-04-17 | 3233.35 |  |  | 700
1983-04-16 | 3232.87 |  |  | 700
1983-04-15 | 3232.63 |  |  | 815
1983-04-14 | 3232.51 |  |  | 1070
1983-04-13 | 3232.57 |  |  | 1210
1983-04-12 | 3232.64 |  |  | 1210
1983-04-11 | 3232.61 |  |  | 1210
1983-04-10 | 3232.56 |  |  | 1210
1983-04-09 | 3232.42 |  |  | 1210
1983-04-08 | 3232.22 |  |  | 1210
1983-04-07 | 3232 |  |  | 1210
1983-04-06 | 3231.85 |  |  | 1440
1983-04-05 | 3231.92 |  |  | 2020
1983-04-04 | 3232.2 |  |  | 2710
1983-04-03 | 3232.8 |  |  | 3190
1983-04-02 | 3233.48 |  |  | 3200
1983-04-01 | 3234.08 |  |  | 3210
1983-03-31 | 3234.6 |  |  | 3210
1983-03-30 | 3234.2 |  |  | 2190
1983-03-29 | 3233.5 |  |  | 840
1983-03-28 | 3232.2 |  |  | 733
1983-03-27 | 3232.84 |  |  | 620
1983-03-26 | 3232.5 |  |  | 619
1983-03-25 | 3232.16 |  |  | 616
1983-03-24 | 3231.7 |  |  | 616
1983-03-23 | 3231.18 |  |  | 615
1983-03-22 | 3230.5 |  |  | 1410
1983-03-21 | 3229.9 |  |  | 2110
1983-03-20 | 3230.16 |  |  | 2560
1983-03-19 | 3230.92 |  |  | 2560
1983-03-18 | 3231.53 |  |  | 2790
1983-03-17 | 3232.02 |  |  | 3190
1983-03-16 | 3232.8 |  |  | 3200
1983-03-15 | 3233.32 |  |  | 3200
1983-03-14 | 3233.2 |  |  | 3190
1983-03-13 | 3232.2 |  |  | 3180
1983-03-12 | 3230.8 |  |  | 3170
1983-03-11 | 3230.2 |  |  | 2940
1983-03-10 | 3229.4 |  |  | 2540
1983-03-09 | 3228.2 |  |  | 2340
1983-03-08 | 3226.68 |  |  | 1980
1983-03-07 | 3226 |  |  | 1720
1983-03-06 | 3225.3 |  |  | 1280
1983-03-05 | 3224 |  |  | 1280
1983-03-04 | 3222.1 |  |  | 1270
1983-03-03 | 3220.63 |  |  | 1370
1983-03-02 | 3219.7 |  |  | 1520
1983-03-01 | 3219.12 |  |  | 1510
1983-02-28 | 3219.08 |  |  | 2260
1983-02-27 | 3219.8 |  |  | 3060
1983-02-26 | 3220.84 |  |  | 3070
1983-02-25 | 3221.58 |  |  | 3110
1983-02-24 | 3221.7 |  |  | 3110
1983-02-23 | 3221.28 |  |  | 2530
1983-02-22 | 3220.1 |  |  | 1590
1983-02-21 | 3218.16 |  |  | 1650
1983-02-20 | 3218.28 |  |  | 1800
1983-02-19 | 3218.2 |  |  | 1580
1983-02-18 | 3217.36 |  |  | 1270
1983-02-17 | 3216.4 |  |  | 1130
1983-02-16 | 3216.03 |  |  | 880
1983-02-15 | 3215.48 |  |  | 480
1983-02-14 | 3214.92 |  |  | 169
1983-02-13 | 3214.08 |  |  | 169
1983-02-12 | 3213.04 |  |  | 169
1983-02-11 | 3212.28 |  |  | 169
1983-02-10 | 3211.68 |  |  | 170
1983-02-09 | 3211.58 |  |  | 171
1983-02-08 | 3211.48 |  |  | 204
1983-02-07 | 3211.46 |  |  | 265
1983-02-06 | 3211.46 |  |  | 265
1983-02-05 | 3211.48 |  |  | 265
1983-02-04 | 3211.48 |  |  | 353
1983-02-03 | 3211.62 |  |  | 536
1983-02-02 | 3211.94 |  |  | 536
1983-02-01 | 3212.01 |  |  | 536
1983-01-31 | 3212.12 |  |  | 495
1983-01-30 | 3212.07 |  |  | 445
1983-01-29 | 3212.02 |  |  | 445
1983-01-28 | 3211.91 |  |  | 402
1983-01-27 | 3211.62 |  |  | 349
1983-01-26 | 3211.5 |  |  | 349
1983-01-25 | 3211.45 |  |  | 407
1983-01-24 | 3211.5 |  |  | 508
1983-01-23 | 3211.6 |  |  | 508
1983-01-22 | 3211.82 |  |  | 508
1983-01-21 | 3211.94 |  |  | 434
1983-01-20 | 3211.82 |  |  | 324
1983-01-19 | 3211.63 |  |  | 324
1983-01-18 | 3211.6 |  |  | 324
1983-01-17 | 3211.6 |  |  | 379
1983-01-16 | 3211.74 |  |  | 420
1983-01-15 | 3211.8 |  |  | 420
1983-01-14 | 3211.98 |  |  | 420
1983-01-13 | 3212 |  |  | 230
1983-01-12 | 3211.75 |  |  | 91
1983-01-11 | 3211.44 |  |  | 879
1983-01-10 | 3211.96 |  |  | 1410
1983-01-09 | 3212.7 |  |  | 1420
1983-01-08 | 3213.2 |  |  | 1120
1983-01-07 | 3213.02 |  |  | 514
1983-01-06 | 3212.4 |  |  | 119
1983-01-05 | 3211.32 |  |  | 84
1983-01-04 | 3211.2 |  |  | 84
1983-01-03 | 3211.12 |  |  | 84
1983-01-02 | 3211.1 |  |  | 83
1983-01-01 | 3211.1 |  |  | 83
1982-12-31 | 3211.08 |  |  | 141
1982-12-30 | 3211.08 |  |  | 219
1982-12-29 | 3211.1 |  |  | 323
1982-12-28 | 3211.28 |  |  | 473
1982-12-27 | 3211.6 |  |  | 473
1982-12-26 | 3211.82 |  |  | 473
1982-12-25 | 3212.1 |  |  | 474
1982-12-24 | 3212.34 |  |  | 476
1982-12-23 | 3212.5 |  |  | 476
1982-12-22 | 3212.53 |  |  | 476
1982-12-21 | 3212.58 |  |  | 476
1982-12-20 | 3212.59 |  |  | 476
1982-12-19 | 3212.6 |  |  | 476
1982-12-18 | 3212.65 |  |  | 476
1982-12-17 | 3212.7 |  |  | 476
1982-12-16 | 3212.9 |  |  | 365
1982-12-15 | 3212.96 |  |  | 268
1982-12-14 | 3213 |  |  | 145
1982-12-13 | 3212.95 |  |  | 11
1982-12-12 | 3212.8 |  |  | 11
1982-12-11 | 3212.62 |  |  | 11
1982-12-10 | 3212.42 |  |  | 11
1982-12-09 | 3212.25 |  |  | 11
1982-12-08 | 3212.15 |  |  | 11
1982-12-07 | 3211.9 |  |  | 11
1982-12-06 | 3211.54 |  |  | 60
1982-12-05 | 3211.1 |  |  | 127
1982-12-04 | 3210.85 |  |  | 126
1982-12-03 | 3210.83 |  |  | 108
1982-12-02 | 3210.8 |  |  | 97
1982-12-01 | 3210.78 |  |  | 97
1982-11-30 | 3210.75 |  |  | 116
1982-11-29 | 3210.72 |  |  | 141
1982-11-28 | 3210.65 |  |  | 141
1982-11-27 | 3210.65 |  |  | 141
1982-11-26 | 3210.65 |  |  | 141
1982-11-25 | 3210.75 |  |  | 141
1982-11-24 | 3210.8 |  |  | 141
1982-11-23 | 3210.82 |  |  | 141
1982-11-22 | 3210.82 |  |  | 141
1982-11-21 | 3210.78 |  |  | 141
1982-11-20 | 3210.8 |  |  | 141
1982-11-19 | 3210.8 |  |  | 346
1982-11-18 | 3211.15 |  |  | 562
1982-11-17 | 3211.6 |  |  | 392
1982-11-16 | 3211.72 |  |  | 216
1982-11-15 | 3211.78 |  |  | 437
1982-11-14 | 3212.15 |  |  | 568
1982-11-13 | 3212.65 |  |  | 568
1982-11-12 | 3213.2 |  |  | 526
1982-11-11 | 3213.72 |  |  | 466
1982-11-10 | 3214 |  |  | 468
1982-11-09 | 3214.28 |  |  | 469
1982-11-08 | 3214.64 |  |  | 469
1982-11-07 | 3214.96 |  |  | 469
1982-11-06 | 3215.2 |  |  | 469
1982-11-05 | 3215.44 |  |  | 469
1982-11-04 | 3215.8 |  |  | 325
1982-11-03 | 3215.85 |  |  | 239
1982-11-02 | 3215.9 |  |  | 415
1982-11-01 | 3216.16 |  |  | 373
1982-10-31 | 3216.32 |  |  | 256
1982-10-30 | 3216.34 |  |  | 247
1982-10-29 | 3216.35 |  |  | 249
1982-10-28 | 3216.38 |  |  | 249
1982-10-27 | 3216.46 |  |  | 249
1982-10-26 | 3216.6 |  |  | 249
1982-10-25 | 3216.7 |  |  | 249
1982-10-24 | 3216.84 |  |  | 249
1982-10-23 | 3217.1 |  |  | 249
1982-10-22 | 3217.2 |  |  | 249
1982-10-21 | 3217.35 |  |  | 249
1982-10-20 | 3217.46 |  |  | 249
1982-10-19 | 3217.58 |  |  | 145
1982-10-18 | 3217.6 |  |  | 160
1982-10-17 | 3217.72 |  |  | 227
1982-10-16 | 3217.8 |  |  | 227
1982-10-15 | 3218 |  |  | 227
1982-10-14 | 3218.1 |  |  | 227
1982-10-13 | 3218.2 |  |  | 227
1982-10-12 | 3218.38 |  |  | 227
1982-10-11 | 3218.5 |  |  | 227
1982-10-10 | 3218.6 |  |  | 227
1982-10-09 | 3218.7 |  |  | 227
1982-10-08 | 3218.8 |  |  | 240
1982-10-07 | 3218.95 |  |  | 266
1982-10-06 | 3219.18 |  |  | 266
1982-10-05 | 3219.37 |  |  | 266
1982-10-04 | 3219.52 |  |  | 266
1982-10-03 | 3219.7 |  |  | 266
1982-10-02 | 3219.85 |  |  | 267
1982-10-01 | 3220.05 |  |  | 267
1982-09-30 | 3220.2 |  |  | 263
1982-09-29 | 3220.38 |  |  | 263
1982-09-28 | 3220.58 |  |  | 263
1982-09-27 | 3220.74 |  |  | 246
1982-09-26 | 3220.92 |  |  | 220
1982-09-25 | 3221.2 |  |  | 220
1982-09-24 | 3221.24 |  |  | 220
1982-09-23 | 3221.4 |  |  | 220
1982-09-22 | 3221.48 |  |  | 220
1982-09-21 | 3221.6 |  |  | 220
1982-09-20 | 3221.8 |  |  | 220
1982-09-19 | 3221.84 |  |  | 220
1982-09-18 | 3222 |  |  | 220
1982-09-17 | 3222.15 |  |  | 220
1982-09-16 | 3222.34 |  |  | 220
1982-09-15 | 3222.48 |  |  | 220
1982-09-14 | 3222.64 |  |  | 220
1982-09-13 | 3222.82 |  |  | 221
1982-09-12 | 3223.05 |  |  | 222
1982-09-11 | 3223.24 |  |  | 222
1982-09-10 | 3223.4 |  |  | 222
1982-09-09 | 3223.62 |  |  | 222
1982-09-08 | 3223.8 |  |  | 222
1982-09-07 | 3223.98 |  |  | 222
1982-09-06 | 3224.22 |  |  | 222
1982-09-05 | 3224.38 |  |  | 222
1982-09-04 | 3224.58 |  |  | 222
1982-09-03 | 3224.7 |  |  | 222
1982-09-02 | 3224.8 |  |  | 222
1982-09-01 | 3225 |  |  | 222
1982-08-31 | 3225.16 |  |  | 222
1982-08-30 | 3225.28 |  |  | 222
1982-08-29 | 3225.48 |  |  | 222
1982-08-28 | 3225.64 |  |  | 222
1982-08-27 | 3225.84 |  |  | 239
1982-08-26 | 3226.08 |  |  | 265
1982-08-25 | 3226.28 |  |  | 265
1982-08-24 | 3226.52 |  |  | 265
1982-08-23 | 3226.78 |  |  | 265
1982-08-22 | 3227.02 |  |  | 265
1982-08-21 | 3227.22 |  |  | 266
1982-08-20 | 3227.4 |  |  | 267
1982-08-19 | 3227.55 |  |  | 267
1982-08-18 | 3227.74 |  |  | 267
1982-08-17 | 3227.88 |  |  | 267
1982-08-16 | 3228.1 |  |  | 269
1982-08-15 | 3228.25 |  |  | 270
1982-08-14 | 3228.42 |  |  | 270
1982-08-13 | 3228.63 |  |  | 270
1982-08-12 | 3228.82 |  |  | 272
1982-08-11 | 3229.05 |  |  | 272
1982-08-10 | 3229.25 |  |  | 273
1982-08-09 | 3229.5 |  |  | 274
1982-08-08 | 3229.76 |  |  | 276
1982-08-07 | 3230 |  |  | 276
1982-08-06 | 3230.2 |  |  | 279
1982-08-05 | 3230.35 |  |  | 280
1982-08-04 | 3230.55 |  |  | 281
1982-08-03 | 3230.62 |  |  | 284
1982-08-02 | 3230.8 |  |  | 287
1982-08-01 | 3231 |  |  | 287
1982-07-31 | 3231.22 |  |  | 257
1982-07-30 | 3231.41 |  |  | 244
1982-07-29 | 3231.6 |  |  | 244
1982-07-28 | 3231.7 |  |  | 246
1982-07-27 | 3231.83 |  |  | 247
1982-07-26 | 3232 |  |  | 249
1982-07-25 | 3232.18 |  |  | 249
1982-07-24 | 3232.28 |  |  | 249
1982-07-23 | 3232.4 |  |  | 275
1982-07-22 | 3232.56 |  |  | 301
1982-07-21 | 3232.72 |  |  | 301
1982-07-20 | 3232.92 |  |  | 303
1982-07-19 | 3233.12 |  |  | 304
1982-07-18 | 3233.28 |  |  | 304
1982-07-17 | 3233.4 |  |  | 304
1982-07-16 | 3233.5 |  |  | 304
1982-07-15 | 3233.7 |  |  | 305
1982-07-14 | 3233.74 |  |  | 306
1982-07-13 | 3233.82 |  |  | 306
1982-07-12 | 3234 |  |  | 306
1982-07-11 | 3234.08 |  |  | 306
1982-07-10 | 3234.18 |  |  | 306
1982-07-09 | 3234.2 |  |  | 273
1982-07-08 | 3234.21 |  |  | 231
1982-07-07 | 3234.22 |  |  | 231
1982-07-06 | 3234.22 |  |  | 231
1982-07-05 | 3234.2 |  |  | 231
1982-07-04 | 3234.2 |  |  | 231
1982-07-03 | 3234.21 |  |  | 231
1982-07-02 | 3234.21 |  |  | 230
1982-07-01 | 3234.2 |  |  | 229
1982-06-30 | 3234.2 |  |  | 229
1982-06-29 | 3234.22 |  |  | 229
1982-06-28 | 3234.24 |  |  | 227
1982-06-27 | 3234.32 |  |  | 227
1982-06-26 | 3234.38 |  |  | 266
1982-06-25 | 3234.48 |  |  | 301
1982-06-24 | 3234.58 |  |  | 301
1982-06-23 | 3234.66 |  |  | 301
1982-06-22 | 3234.72 |  |  | 300
1982-06-21 | 3234.78 |  |  | 299
1982-06-20 | 3234.88 |  |  | 299
1982-06-19 | 3235 |  |  | 299
1982-06-18 | 3235.15 |  |  | 301
1982-06-17 | 3235.22 |  |  | 301
1982-06-16 | 3235.25 |  |  | 304
1982-06-15 | 3235.28 |  |  | 304
1982-06-14 | 3235.26 |  |  | 303
1982-06-13 | 3235.22 |  |  | 301
1982-06-12 | 3235.2 |  |  | 301
1982-06-11 | 3235.22 |  |  | 364
1982-06-10 | 3235.38 |  |  | 401
1982-06-09 | 3235.45 |  |  | 405
1982-06-08 | 3235.44 |  |  | 408
1982-06-07 | 3235.43 |  |  | 410
1982-06-06 | 3235.42 |  |  | 412
1982-06-05 | 3235.42 |  |  | 409
1982-06-04 | 3235.42 |  |  | 408
1982-06-03 | 3235.4 |  |  | 406
1982-06-02 | 3235.38 |  |  | 401
1982-06-01 | 3235.28 |  |  | 398
1982-05-31 | 3235.28 |  |  | 396
1982-05-30 | 3235.25 |  |  | 396
1982-05-29 | 3235.22 |  |  | 394
1982-05-28 | 3235.2 |  |  | 469
1982-05-27 | 3235.28 |  |  | 596
1982-05-26 | 3235.35 |  |  | 635
1982-05-25 | 3235.4 |  |  | 636
1982-05-24 | 3235.42 |  |  | 717
1982-05-23 | 3235.55 |  |  | 856
1982-05-22 | 3235.6 |  |  | 864
1982-05-21 | 3235.64 |  |  | 871
1982-05-20 | 3235.64 |  |  | 876
1982-05-19 | 3235.64 |  |  | 875
1982-05-18 | 3235.62 |  |  | 866
1982-05-17 | 3235.52 |  |  | 862
1982-05-16 | 3235.52 |  |  | 860
1982-05-15 | 3235.5 |  |  | 860
1982-05-14 | 3235.5 |  |  | 607
1982-05-13 | 3235.3 |  |  | 725
1982-05-12 | 3235.28 |  |  | 1070
1982-05-11 | 3235.08 |  |  | 1120
1982-05-10 | 3235.08 |  |  | 1120
1982-05-09 | 3235.08 |  |  | 1120
1982-05-08 | 3235.08 |  |  | 1120
1982-05-07 | 3235.08 |  |  | 1120
1982-05-06 | 3235.08 |  |  | 1210
1982-05-05 | 3235.08 |  |  | 1480
1982-05-04 | 3235.11 |  |  | 1640
1982-05-03 | 3235.3 |  |  | 1790
1982-05-02 | 3235.37 |  |  | 1870
1982-05-01 | 3235.45 |  |  | 1930
1982-04-30 | 3235.55 |  |  | 1660
1982-04-29 | 3235.25 |  |  | 1700
1982-04-28 | 3235.05 |  |  | 2020
1982-04-27 | 3234.8 |  |  | 1940
1982-04-26 | 3234.58 |  |  | 1460
1982-04-25 | 3234.15 |  |  | 1180
1982-04-24 | 3233.4 |  |  | 1180
1982-04-23 | 3232.5 |  |  | 1050
1982-04-22 | 3231.77 |  |  | 958
1982-04-21 | 3231.25 |  |  | 1130
1982-04-20 | 3231.2 |  |  | 1230
1982-04-19 | 3231.75 |  |  | 1560
1982-04-18 | 3231.75 |  |  | 1760
1982-04-17 | 3231.75 |  |  | 1770
1982-04-16 | 3231.75 |  |  | 1770
1982-04-15 | 3231.75 |  |  | 1770
1982-04-14 | 3231.45 |  |  | 1770
1982-04-13 | 3231.15 |  |  | 1620
1982-04-12 | 3230.53 |  |  | 946
1982-04-11 | 3229.42 |  |  | 584
1982-04-10 | 3227.4 |  |  | 582
1982-04-09 | 3227.2 |  |  | 580
1982-04-08 | 3227.1 |  |  | 580
1982-04-07 | 3227 |  |  | 580
1982-04-06 | 3226.85 |  |  | 580
1982-04-05 | 3226.75 |  |  | 580
1982-04-04 | 3226.62 |  |  | 580
1982-04-03 | 3226.43 |  |  | 580
1982-04-02 | 3226.2 |  |  | 581
1982-04-01 | 3226 |  |  | 580
1982-03-31 | 3225.65 |  |  | 262
1982-03-30 | 3225.15 |  |  | 368
1982-03-29 | 3224.71 |  |  | 523
1982-03-28 | 3224.2 |  |  | 521
1982-03-27 | 3223.6 |  |  | 521
1982-03-26 | 3222.85 |  |  | 942
1982-03-25 | 3222.85 |  |  | 1250
1982-03-24 | 3223.05 |  |  | 1250
1982-03-23 | 3223.3 |  |  | 1260
1982-03-22 | 3223.6 |  |  | 1260
1982-03-21 | 3224 |  |  | 1260
1982-03-20 | 3224.35 |  |  | 1260
1982-03-19 | 3224.7 |  |  | 1270
1982-03-18 | 3224.95 |  |  | 1270
1982-03-17 | 3225.15 |  |  | 1270
1982-03-16 | 3225.15 |  |  | 1270
1982-03-15 | 3225.15 |  |  | 1270
1982-03-14 | 3225.05 |  |  | 1270
1982-03-13 | 3224.97 |  |  | 1270
1982-03-12 | 3224.95 |  |  | 1270
1982-03-11 | 3224.7 |  |  | 1450
1982-03-10 | 3224.55 |  |  | 1670
1982-03-09 | 3224.9 |  |  | 859
1982-03-08 | 3224.55 |  |  | 1120
1982-03-07 | 3224.57 |  |  | 1630
1982-03-06 | 3224.97 |  |  | 1630
1982-03-05 | 3225.5 |  |  | 1630
1982-03-04 | 3225.55 |  |  | 1630
1982-03-03 | 3225.55 |  |  | 1630
1982-03-02 | 3225.53 |  |  | 1630
1982-03-01 | 3225.5 |  |  | 1630
1982-02-28 | 3225.57 |  |  | 2540
1982-02-27 | 3226.37 |  |  | 3130
1982-02-26 | 3227.57 |  |  | 3010
1982-02-25 | 3228.63 |  |  | 3130
1982-02-24 | 3229.61 |  |  | 3150
1982-02-23 | 3230.3 |  |  | 3150
1982-02-22 | 3230.1 |  |  | 3140
1982-02-21 | 3229.04 |  |  | 3120
1982-02-20 | 3225.5 |  |  | 2900
1982-02-19 | 3222.98 |  |  | 2540
1982-02-18 | 3221.18 |  |  | 2050
1982-02-17 | 3219.82 |  |  | 1530
1982-02-16 | 3216.4 |  |  | 1200
1982-02-15 | 3212.75 |  |  | 632
1982-02-14 | 3211.15 |  |  | 256
1982-02-13 | 3210.84 |  |  | 256
1982-02-12 | 3210.8 |  |  | 244
1982-02-11 | 3210.77 |  |  | 236
1982-02-10 | 3210.76 |  |  | 236
1982-02-09 | 3210.75 |  |  | 273
1982-02-08 | 3210.8 |  |  | 327
1982-02-07 | 3210.8 |  |  | 324
1982-02-06 | 3210.8 |  |  | 324
1982-02-05 | 3210.81 |  |  | 364
1982-02-04 | 3210.92 |  |  | 475
1982-02-03 | 3211 |  |  | 520
1982-02-02 | 3211 |  |  | 575
1982-02-01 | 3211.1 |  |  | 702
1982-01-31 | 3211.26 |  |  | 775
1982-01-30 | 3211.44 |  |  | 776
1982-01-29 | 3211.54 |  |  | 1120
1982-01-28 | 3212.1 |  |  | 1240
1982-01-27 | 3212.2 |  |  | 1030
1982-01-26 | 3212 |  |  | 669
1982-01-25 | 3211.62 |  |  | 431
1982-01-24 | 3211.24 |  |  | 329
1982-01-23 | 3211.12 |  |  | 331
1982-01-22 | 3211.05 |  |  | 330
1982-01-21 | 3211.05 |  |  | 330
1982-01-20 | 3211.05 |  |  | 330
1982-01-19 | 3211.05 |  |  | 329
1982-01-18 | 3211.05 |  |  | 341
1982-01-17 | 3211.06 |  |  | 357
1982-01-16 | 3211.07 |  |  | 357
1982-01-15 | 3211.08 |  |  | 523
1982-01-14 | 3211.34 |  |  | 738
1982-01-13 | 3211.8 |  |  | 485
1982-01-12 | 3211.82 |  |  | 338
1982-01-11 | 3211.82 |  |  | 278
1982-01-10 | 3211.78 |  |  | 208
1982-01-09 | 3211.64 |  |  | 208
1982-01-08 | 3211.54 |  |  | 208
1982-01-07 | 3211.52 |  |  | 208
1982-01-06 | 3211.5 |  |  | 476
1982-01-05 | 3211.82 |  |  | 688
1982-01-04 | 3212.18 |  |  | 339
1982-01-03 | 3211.98 |  |  | 124
1982-01-02 | 3211.76 |  |  | 124
1982-01-01 | 3211.5 |  |  | 124
1981-12-31 | 3211.24 |  |  | 487
1981-12-30 | 3211.4 |  |  | 915
1981-12-29 | 3211.96 |  |  | 1250
1981-12-28 | 3212.8 |  |  | 1660
1981-12-27 | 3213.7 |  |  | 1670
1981-12-26 | 3214.76 |  |  | 1670
1981-12-25 | 3215.72 |  |  | 1680
1981-12-24 | 3216.44 |  |  | 1680
1981-12-23 | 3217.2 |  |  | 1690
1981-12-22 | 3217.8 |  |  | 1700
1981-12-21 | 3217.82 |  |  | 1490
1981-12-20 | 3216.96 |  |  | 1230
1981-12-19 | 3214.05 |  |  | 1160
1981-12-18 | 3212.22 |  |  | 979
1981-12-17 | 3212.4 |  |  | 624
1981-12-16 | 3212 |  |  | 390
1981-12-15 | 3211.5 |  |  | 591
1981-12-14 | 3211.4 |  |  | 360
1981-12-13 | 3211.44 |  |  | 144
1981-12-12 | 3211.1 |  |  | 191
1981-12-11 | 3211.1 |  |  | 663
1981-12-10 | 3211.44 |  |  | 1390
1981-12-09 | 3212.35 |  |  | 1400
1981-12-08 | 3213.2 |  |  | 1100
1981-12-07 | 3213.6 |  |  | 410
1981-12-06 | 3213.2 |  |  | 173
1981-12-05 | 3212.58 |  |  | 174
1981-12-04 | 3212.58 |  |  | 174
1981-12-03 | 3212.6 |  |  | 174
1981-12-02 | 3212.6 |  |  | 174
1981-12-01 | 3212.59 |  |  | 174
1981-11-30 | 3212.58 |  |  | 174
1981-11-29 | 3212.62 |  |  | 174
1981-11-28 | 3212.6 |  |  | 163
1981-11-27 | 3212.5 |  |  | 157
1981-11-26 | 3212.5 |  |  | 157
1981-11-25 | 3212.5 |  |  | 157
1981-11-24 | 3212.47 |  |  | 134
1981-11-23 | 3212.3 |  |  | 120
1981-11-22 | 3212.3 |  |  | 120
1981-11-21 | 3212.3 |  |  | 120
1981-11-20 | 3212.3 |  |  | 120
1981-11-19 | 3212.23 |  |  | 120
1981-11-18 | 3212.21 |  |  | 120
1981-11-17 | 3212.22 |  |  | 66
1981-11-16 | 3212.12 |  |  | 33
1981-11-15 | 3212 |  |  | 32
1981-11-14 | 3212 |  |  | 32
1981-11-13 | 3211.98 |  |  | 33
1981-11-12 | 3211.9 |  |  | 33
1981-11-11 | 3211.84 |  |  | 33
1981-11-10 | 3211.8 |  |  | 33
1981-11-09 | 3211.76 |  |  | 33
1981-11-08 | 3211.74 |  |  | 33
1981-11-07 | 3211.64 |  |  | 33
1981-11-06 | 3211.62 |  |  | 33
1981-11-05 | 3211.6 |  |  | 93
1981-11-04 | 3211.72 |  |  | 129
1981-11-03 | 3211.8 |  |  | 130
1981-11-02 | 3211.86 |  |  | 130
1981-11-01 | 3211.92 |  |  | 130
1981-10-31 | 3211.95 |  |  | 159
1981-10-30 | 3212.02 |  |  | 167
1981-10-29 | 3212.14 |  |  | 169
1981-10-28 | 3212.2 |  |  | 151
1981-10-27 | 3212.4 |  |  | 167
1981-10-26 | 3212.55 |  |  | 167
1981-10-25 | 3212.58 |  |  | 169
1981-10-24 | 3212.58 |  |  | 111
1981-10-23 | 3212.55 |  |  | 21
1981-10-22 | 3212.55 |  |  | 117
1981-10-21 | 3212.73 |  |  | 169
1981-10-20 | 3212.75 |  |  | 108
1981-10-19 | 3212.76 |  |  | 108
1981-10-18 | 3212.88 |  |  | 141
1981-10-17 | 3212.9 |  |  | 140
1981-10-16 | 3212.9 |  |  | 140
1981-10-15 | 3213.02 |  |  | 140
1981-10-14 | 3213.08 |  |  | 141
1981-10-13 | 3213.12 |  |  | 141
1981-10-12 | 3213.13 |  |  | 141
1981-10-11 | 3213.2 |  |  | 140
1981-10-10 | 3213.25 |  |  | 140
1981-10-09 | 3213.3 |  |  | 168
1981-10-08 | 3213.4 |  |  | 185
1981-10-07 | 3213.55 |  |  | 184
1981-10-06 | 3213.65 |  |  | 184
1981-10-05 | 3213.77 |  |  | 184
1981-10-04 | 3213.95 |  |  | 184
1981-10-03 | 3214.05 |  |  | 182
1981-10-02 | 3214.2 |  |  | 182
1981-10-01 | 3214.4 |  |  | 182
1981-09-30 | 3214.53 |  |  | 186
1981-09-29 | 3214.65 |  |  | 191
1981-09-28 | 3214.8 |  |  | 191
1981-09-27 | 3215 |  |  | 191
1981-09-26 | 3215.15 |  |  | 191
1981-09-25 | 3215.25 |  |  | 195
1981-09-24 | 3215.53 |  |  | 201
1981-09-23 | 3215.7 |  |  | 201
1981-09-22 | 3215.87 |  |  | 201
1981-09-21 | 3216 |  |  | 206
1981-09-20 | 3216.21 |  |  | 212
1981-09-19 | 3216.4 |  |  | 212
1981-09-18 | 3216.63 |  |  | 212
1981-09-17 | 3216.85 |  |  | 212
1981-09-16 | 3217 |  |  | 212
1981-09-15 | 3217.25 |  |  | 212
1981-09-14 | 3217.4 |  |  | 212
1981-09-13 | 3217.6 |  |  | 212
1981-09-12 | 3217.83 |  |  | 212
1981-09-11 | 3217.95 |  |  | 212
1981-09-10 | 3218.25 |  |  | 212
1981-09-09 | 3218.45 |  |  | 212
1981-09-08 | 3218.65 |  |  | 210
1981-09-07 | 3218.85 |  |  | 212
1981-09-06 | 3219 |  |  | 212
1981-09-05 | 3219.15 |  |  | 214
1981-09-04 | 3219.23 |  |  | 214
1981-09-03 | 3219.45 |  |  | 214
1981-09-02 | 3219.6 |  |  | 214
1981-09-01 | 3219.8 |  |  | 249
1981-08-31 | 3220 |  |  | 269
1981-08-30 | 3220.2 |  |  | 269
1981-08-29 | 3220.45 |  |  | 272
1981-08-28 | 3220.67 |  |  | 272
1981-08-27 | 3220.95 |  |  | 272
1981-08-26 | 3221.2 |  |  | 272
1981-08-25 | 3221.55 |  |  | 272
1981-08-24 | 3221.75 |  |  | 272
1981-08-23 | 3221.95 |  |  | 272
1981-08-22 | 3222.15 |  |  | 274
1981-08-21 | 3222.45 |  |  | 274
1981-08-20 | 3222.75 |  |  | 274
1981-08-19 | 3223.03 |  |  | 274
1981-08-18 | 3223.25 |  |  | 274
1981-08-17 | 3223.5 |  |  | 276
1981-08-16 | 3223.67 |  |  | 276
1981-08-15 | 3223.9 |  |  | 276
1981-08-14 | 3224.15 |  |  | 276
1981-08-13 | 3224.3 |  |  | 276
1981-08-12 | 3224.5 |  |  | 276
1981-08-11 | 3224.83 |  |  | 276
1981-08-10 | 3225 |  |  | 279
1981-08-09 | 3225.15 |  |  | 279
1981-08-08 | 3225.33 |  |  | 279
1981-08-07 | 3225.6 |  |  | 279
1981-08-06 | 3225.8 |  |  | 279
1981-08-05 | 3225.95 |  |  | 279
1981-08-04 | 3226.15 |  |  | 279
1981-08-03 | 3226.35 |  |  | 279
1981-08-02 | 3226.57 |  |  | 281
1981-08-01 | 3226.83 |  |  | 281
1981-07-31 | 3227.1 |  |  | 281
1981-07-30 | 3227.33 |  |  | 281
1981-07-29 | 3227.57 |  |  | 281
1981-07-28 | 3227.85 |  |  | 281
1981-07-27 | 3228.05 |  |  | 281
1981-07-26 | 3228.2 |  |  | 281
1981-07-25 | 3228.35 |  |  | 281
1981-07-24 | 3228.55 |  |  | 281
1981-07-23 | 3228.8 |  |  | 281
1981-07-22 | 3229 |  |  | 283
1981-07-21 | 3229.17 |  |  | 283
1981-07-20 | 3229.43 |  |  | 283
1981-07-19 | 3229.65 |  |  | 283
1981-07-18 | 3229.83 |  |  | 283
1981-07-17 | 3230.03 |  |  | 286
1981-07-16 | 3230.35 |  |  | 286
1981-07-15 | 3230.53 |  |  | 286
1981-07-14 | 3230.65 |  |  | 286
1981-07-13 | 3230.75 |  |  | 286
1981-07-12 | 3230.95 |  |  | 286
1981-07-11 | 3231.1 |  |  | 286
1981-07-10 | 3231.27 |  |  | 269
1981-07-09 | 3231.5 |  |  | 256
1981-07-08 | 3231.65 |  |  | 256
1981-07-07 | 3231.85 |  |  | 276
1981-07-06 | 3232.03 |  |  | 288
1981-07-05 | 3232.23 |  |  | 288
1981-07-04 | 3232.45 |  |  | 288
1981-07-03 | 3232.65 |  |  | 274
1981-07-02 | 3232.85 |  |  | 251
1981-07-01 | 3233.01 |  |  | 251
1981-06-30 | 3233.17 |  |  | 251
1981-06-29 | 3233.35 |  |  | 251
1981-06-28 | 3233.53 |  |  | 251
1981-06-27 | 3233.61 |  |  | 251
1981-06-26 | 3233.77 |  |  | 251
1981-06-25 | 3233.85 |  |  | 251
1981-06-24 | 3234.05 |  |  | 251
1981-06-23 | 3234.15 |  |  | 251
1981-06-22 | 3234.15 |  |  | 251
1981-06-21 | 3234.45 |  |  | 251
1981-06-20 | 3234.59 |  |  | 251
1981-06-19 | 3234.52 |  |  | 251
1981-06-18 | 3234.62 |  |  | 251
1981-06-17 | 3234.72 |  |  | 251
1981-06-16 | 3234.8 |  |  | 253
1981-06-15 | 3234.92 |  |  | 256
1981-06-14 | 3235 |  |  | 258
1981-06-13 | 3235.02 |  |  | 263
1981-06-12 | 3235.1 |  |  | 265
1981-06-11 | 3235.18 |  |  | 267
1981-06-10 | 3235.2 |  |  | 267
1981-06-09 | 3235.2 |  |  | 267
1981-06-08 | 3235.24 |  |  | 272
1981-06-07 | 3235.32 |  |  | 276
1981-06-06 | 3235.44 |  |  | 286
1981-06-05 | 3235.58 |  |  | 293
1981-06-04 | 3235.68 |  |  | 301
1981-06-03 | 3235.78 |  |  | 311
1981-06-02 | 3235.84 |  |  | 319
1981-06-01 | 3236 |  |  | 329
1981-05-31 | 3236 |  |  | 335
1981-05-30 | 3236.1 |  |  | 343
1981-05-29 | 3236.1 |  |  | 352
1981-05-28 | 3236.08 |  |  | 354
1981-05-27 | 3236.08 |  |  | 352
1981-05-26 | 3236 |  |  | 338
1981-05-25 | 3235.88 |  |  | 322
1981-05-24 | 3235.86 |  |  | 322
1981-05-23 | 3235.86 |  |  | 327
1981-05-22 | 3235.86 |  |  | 329
1981-05-21 | 3235.8 |  |  | 327
1981-05-20 | 3235.8 |  |  | 319
1981-05-19 | 3235.8 |  |  | 316
1981-05-18 | 3235.8 |  |  | 298
1981-05-17 | 3235.8 |  |  | 276
1981-05-16 | 3235.88 |  |  | 281
1981-05-15 | 3236 |  |  | 293
1981-05-14 | 3236.18 |  |  | 298
1981-05-13 | 3236.3 |  |  | 303
1981-05-12 | 3236.4 |  |  | 314
1981-05-11 | 3236.5 |  |  | 296
1981-05-10 | 3236.57 |  |  | 269
1981-05-09 | 3236.57 |  |  | 274
1981-05-08 | 3236.56 |  |  | 279
1981-05-07 | 3236.64 |  |  | 281
1981-05-06 | 3236.64 |  |  | 283
1981-05-05 | 3236.64 |  |  | 283
1981-05-04 | 3236.64 |  |  | 393
1981-05-03 | 3236.82 |  |  | 476
1981-05-02 | 3236.9 |  |  | 483
1981-05-01 | 3237 |  |  | 616
1981-04-30 | 3237.02 |  |  | 800
1981-04-29 | 3237.15 |  |  | 825
1981-04-28 | 3237.27 |  |  | 850
1981-04-27 | 3237.35 |  |  | 825
1981-04-26 | 3237.33 |  |  | 755
1981-04-25 | 3237.3 |  |  | 750
1981-04-24 | 3237.27 |  |  | 840
1981-04-23 | 3237.31 |  |  | 845
1981-04-22 | 3237.3 |  |  | 765
1981-04-21 | 3237.25 |  |  | 660
1981-04-20 | 3237.07 |  |  | 393
1981-04-19 | 3236.55 |  |  | 281
1981-04-18 | 3236.35 |  |  | 258
1981-04-17 | 3236.25 |  |  | 244
1981-04-16 | 3236.15 |  |  | 231
1981-04-15 | 3236 |  |  | 226
1981-04-14 | 3235.95 |  |  | 220
1981-04-13 | 3235.77 |  |  | 212
1981-04-12 | 3235.75 |  |  | 205
1981-04-11 | 3235.65 |  |  | 195
1981-04-10 | 3235.6 |  |  | 210
1981-04-09 | 3235.51 |  |  | 237
1981-04-08 | 3235.43 |  |  | 269
1981-04-07 | 3235.35 |  |  | 303
1981-04-06 | 3235.33 |  |  | 490
1981-04-05 | 3235.37 |  |  | 600
1981-04-04 | 3235.41 |  |  | 604
1981-04-03 | 3235.41 |  |  | 835
1981-04-02 | 3235.55 |  |  | 925
1981-04-01 | 3235.75 |  |  | 930
1981-03-31 | 3235.8 |  |  | 1070
1981-03-30 | 3236.07 |  |  | 1300
1981-03-29 | 3236.2 |  |  | 1320
1981-03-28 | 3236.3 |  |  | 1340
1981-03-27 | 3236.3 |  |  | 925
1981-03-26 | 3235.85 |  |  | 291
1981-03-25 | 3234.8 |  |  | 143
1981-03-24 | 3234.25 |  |  | 72
1981-03-23 | 3233.75 |  |  | 72
1981-03-22 | 3233.23 |  |  | 71
1981-03-21 | 3232.87 |  |  | 71
1981-03-20 | 3232.55 |  |  | 71
1981-03-19 | 3232.3 |  |  | 71
1981-03-18 | 3232.05 |  |  | 61
1981-03-17 | 3231.77 |  |  | 54
1981-03-16 | 3231.47 |  |  | 54
1981-03-15 | 3231.15 |  |  | 54
1981-03-14 | 3230.75 |  |  | 53
1981-03-13 | 3230.5 |  |  | 53
1981-03-12 | 3230.15 |  |  | 53
1981-03-11 | 3229.97 |  |  | 53
1981-03-10 | 3229.9 |  |  | 53
1981-03-09 | 3229.74 |  |  | 53
1981-03-08 | 3229.46 |  |  | 52
1981-03-07 | 3229.24 |  |  | 52
1981-03-06 | 3229.04 |  |  | 52
1981-03-05 | 3228.74 |  |  | 52
1981-03-04 | 3228.44 |  |  | 52
1981-03-03 | 3228.14 |  |  | 52
1981-03-02 | 3227.76 |  |  | 98
1981-03-01 | 3227.52 |  |  | 128
1981-02-28 | 3227.32 |  |  | 222
1981-02-27 | 3227.14 |  |  | 263
1981-02-26 | 3226.9 |  |  | 493
1981-02-25 | 3226.84 |  |  | 765
1981-02-24 | 3226.84 |  |  | 765
1981-02-23 | 3226.84 |  |  | 636
1981-02-22 | 3226.62 |  |  | 564
1981-02-21 | 3226.26 |  |  | 301
1981-02-20 | 3225.44 |  |  | 89
1981-02-19 | 3223.64 |  |  | 88
1981-02-18 | 3220.6 |  |  | 66
1981-02-17 | 3219.2 |  |  | 33
1981-02-16 | 3216.6 |  |  | 26
1981-02-15 | 3215.2 |  |  | 26
1981-02-14 | 3214.78 |  |  | 26
1981-02-13 | 3214.6 |  |  | 26
1981-02-12 | 3214.5 |  |  | 26
1981-02-11 | 3214.44 |  |  | 26
1981-02-10 | 3214.36 |  |  | 26
1981-02-09 | 3214.26 |  |  | 26
1981-02-08 | 3214.18 |  |  | 26
1981-02-07 | 3214.1 |  |  | 26
1981-02-06 | 3214 |  |  | 26
1981-02-05 | 3213.9 |  |  | 26
1981-02-04 | 3213.8 |  |  | 38
1981-02-03 | 3213.7 |  |  | 52
1981-02-02 | 3213.62 |  |  | 52
1981-02-01 | 3213.6 |  |  | 52
1981-01-31 | 3213.52 |  |  | 52
1981-01-30 | 3213.4 |  |  | 52
1981-01-29 | 3213.3 |  |  | 52
1981-01-28 | 3213.14 |  |  | 52
1981-01-27 | 3213.08 |  |  | 52
1981-01-26 | 3212.95 |  |  | 51
1981-01-25 | 3212.85 |  |  | 51
1981-01-24 | 3212.7 |  |  | 51
1981-01-23 | 3212.54 |  |  | 51
1981-01-22 | 3212.38 |  |  | 51
1981-01-21 | 3212.3 |  |  | 51
1981-01-20 | 3212.22 |  |  | 51
1981-01-19 | 3212.14 |  |  | 51
1981-01-18 | 3212.1 |  |  | 51
1981-01-17 | 3212.1 |  |  | 51
1981-01-16 | 3212.1 |  |  | 30
1981-01-15 | 3212 |  |  | 12
1981-01-14 | 3211.98 |  |  | 12
1981-01-13 | 3211.8 |  |  | 11
1981-01-12 | 3211.76 |  |  | 258
1981-01-11 | 3212 |  |  | 564
1981-01-10 | 3212.32 |  |  | 564
1981-01-09 | 3212.68 |  |  | 564
1981-01-08 | 3213 |  |  | 564
1981-01-07 | 3213.4 |  |  | 568
1981-01-06 | 3213.7 |  |  | 568
1981-01-05 | 3214 |  |  | 411
1981-01-04 | 3214.1 |  |  | 249
1981-01-03 | 3214.1 |  |  | 249
1981-01-02 | 3214.1 |  |  | 249
1981-01-01 | 3214.06 |  |  | 249
1980-12-31 | 3214 |  |  | 652
1980-12-30 | 3214.3 |  |  | 1120
1980-12-29 | 3215.08 |  |  | 990
1980-12-28 | 3215.22 |  |  | 855
1980-12-27 | 3215.22 |  |  | 390
1980-12-26 | 3214.62 |  |  | 96
1980-12-25 | 3212.88 |  |  | 95
1980-12-24 | 3211.82 |  |  | 95
1980-12-23 | 3211.64 |  |  | 95
1980-12-22 | 3211.42 |  |  | 95
1980-12-21 | 3211.4 |  |  | 95
1980-12-20 | 3211.38 |  |  | 94
1980-12-19 | 3211.38 |  |  | 89
1980-12-18 | 3211.38 |  |  | 80
1980-12-17 | 3211.38 |  |  | 80
1980-12-16 | 3211.38 |  |  | 77
1980-12-15 | 3211.32 |  |  | 79
1980-12-14 | 3211.32 |  |  | 79
1980-12-13 | 3211.32 |  |  | 79
1980-12-12 | 3211.32 |  |  | 139
1980-12-11 | 3211.42 |  |  | 173
1980-12-10 | 3211.48 |  |  | 173
1980-12-09 | 3211.58 |  |  | 173
1980-12-08 | 3211.78 |  |  | 173
1980-12-07 | 3211.78 |  |  | 173
1980-12-06 | 3211.78 |  |  | 173
1980-12-05 | 3211.78 |  |  | 128
1980-12-04 | 3211.62 |  |  | 108
1980-12-03 | 3211.58 |  |  | 108
1980-12-02 | 3211.58 |  |  | 108
1980-12-01 | 3211.58 |  |  | 108
1980-11-30 | 3211.58 |  |  | 89
1980-11-29 | 3211.54 |  |  | 77
1980-11-28 | 3211.52 |  |  | 77
1980-11-27 | 3211.52 |  |  | 77
1980-11-26 | 3211.52 |  |  | 77
1980-11-25 | 3211.48 |  |  | 77
1980-11-24 | 3211.48 |  |  | 77
1980-11-23 | 3211.46 |  |  | 77
1980-11-22 | 3211.46 |  |  | 77
1980-11-21 | 3211.46 |  |  | 119
1980-11-20 | 3211.54 |  |  | 180
1980-11-19 | 3211.72 |  |  | 180
1980-11-18 | 3211.88 |  |  | 180
1980-11-17 | 3211.98 |  |  | 180
1980-11-16 | 3212.12 |  |  | 180
1980-11-15 | 3212.14 |  |  | 182
1980-11-14 | 3212.16 |  |  | 182
1980-11-13 | 3212.32 |  |  | 182
1980-11-12 | 3212.4 |  |  | 182
1980-11-11 | 3212.52 |  |  | 182
1980-11-10 | 3212.6 |  |  | 182
1980-11-09 | 3212.67 |  |  | 182
1980-11-08 | 3212.74 |  |  | 182
1980-11-07 | 3212.82 |  |  | 148
1980-11-06 | 3212.84 |  |  | 116
1980-11-05 | 3212.92 |  |  | 116
1980-11-04 | 3212.92 |  |  | 116
1980-11-03 | 3212.96 |  |  | 116
1980-11-02 | 3213 |  |  | 116
1980-11-01 | 3213.02 |  |  | 116
1980-10-31 | 3213.1 |  |  | 154
1980-10-30 | 3213.17 |  |  | 195
1980-10-29 | 3213.32 |  |  | 195
1980-10-28 | 3213.42 |  |  | 195
1980-10-27 | 3213.52 |  |  | 197
1980-10-26 | 3213.64 |  |  | 197
1980-10-25 | 3213.72 |  |  | 197
1980-10-24 | 3213.88 |  |  | 195
1980-10-23 | 3213.98 |  |  | 105
1980-10-22 | 3214 |  |  | 110
1980-10-21 | 3214.1 |  |  | 182
1980-10-20 | 3214.26 |  |  | 182
1980-10-19 | 3214.36 |  |  | 182
1980-10-18 | 3214.5 |  |  | 182
1980-10-17 | 3214.6 |  |  | 182
1980-10-16 | 3214.75 |  |  | 182
1980-10-15 | 3214.9 |  |  | 182
1980-10-14 | 3215 |  |  | 182
1980-10-13 | 3215.16 |  |  | 182
1980-10-12 | 3215.3 |  |  | 182
1980-10-11 | 3215.4 |  |  | 182
1980-10-10 | 3215.5 |  |  | 182
1980-10-09 | 3215.6 |  |  | 182
1980-10-08 | 3215.8 |  |  | 182
1980-10-07 | 3215.96 |  |  | 184
1980-10-06 | 3216.08 |  |  | 184
1980-10-05 | 3216.2 |  |  | 184
1980-10-04 | 3216.3 |  |  | 184
1980-10-03 | 3216.43 |  |  | 184
1980-10-02 | 3216.57 |  |  | 184
1980-10-01 | 3216.72 |  |  | 184
1980-09-30 | 3216.88 |  |  | 178
1980-09-29 | 3217.02 |  |  | 178
1980-09-28 | 3217.2 |  |  | 178
1980-09-27 | 3217.36 |  |  | 178
1980-09-26 | 3217.48 |  |  | 178
1980-09-25 | 3217.62 |  |  | 178
1980-09-24 | 3217.8 |  |  | 178
1980-09-23 | 3217.92 |  |  | 178
1980-09-22 | 3218.08 |  |  | 178
1980-09-21 | 3218.22 |  |  | 178
1980-09-20 | 3218.36 |  |  | 178
1980-09-19 | 3218.42 |  |  | 187
1980-09-18 | 3218.58 |  |  | 205
1980-09-17 | 3218.72 |  |  | 205
1980-09-16 | 3218.88 |  |  | 205
1980-09-15 | 3219 |  |  | 205
1980-09-14 | 3219.16 |  |  | 205
1980-09-13 | 3219.3 |  |  | 205
1980-09-12 | 3219.5 |  |  | 222
1980-09-11 | 3219.7 |  |  | 242
1980-09-10 | 3219.92 |  |  | 242
1980-09-09 | 3220.12 |  |  | 242
1980-09-08 | 3220.36 |  |  | 242
1980-09-07 | 3220.6 |  |  | 242
1980-09-06 | 3220.91 |  |  | 242
1980-09-05 | 3221.06 |  |  | 242
1980-09-04 | 3221.26 |  |  | 242
1980-09-03 | 3221.42 |  |  | 242
1980-09-02 | 3221.62 |  |  | 244
1980-09-01 | 3221.82 |  |  | 244
1980-08-31 | 3222 |  |  | 244
1980-08-30 | 3222.24 |  |  | 244
1980-08-29 | 3222.46 |  |  | 244
1980-08-28 | 3222.64 |  |  | 246
1980-08-27 | 3222.86 |  |  | 246
1980-08-26 | 3223.1 |  |  | 246
1980-08-25 | 3223.26 |  |  | 249
1980-08-24 | 3223.48 |  |  | 251
1980-08-23 | 3223.76 |  |  | 251
1980-08-22 | 3224.02 |  |  | 253
1980-08-21 | 3224.24 |  |  | 253
1980-08-20 | 3224.4 |  |  | 253
1980-08-19 | 3224.54 |  |  | 253
1980-08-18 | 3224.7 |  |  | 256
1980-08-17 | 3224.96 |  |  | 256
1980-08-16 | 3225.16 |  |  | 256
1980-08-15 | 3225.3 |  |  | 256
1980-08-14 | 3225.6 |  |  | 256
1980-08-13 | 3225.82 |  |  | 258
1980-08-12 | 3226.02 |  |  | 258
1980-08-11 | 3226.22 |  |  | 258
1980-08-10 | 3226.44 |  |  | 258
1980-08-09 | 3226.64 |  |  | 258
1980-08-08 | 3226.84 |  |  | 258
1980-08-07 | 3227.1 |  |  | 258
1980-08-06 | 3227.28 |  |  | 258
1980-08-05 | 3227.49 |  |  | 258
1980-08-04 | 3227.6 |  |  | 258
1980-08-03 | 3227.82 |  |  | 258
1980-08-02 | 3228.02 |  |  | 258
1980-08-01 | 3228.22 |  |  | 258
1980-07-31 | 3228.42 |  |  | 276
1980-07-30 | 3228.62 |  |  | 309
1980-07-29 | 3228.88 |  |  | 309
1980-07-28 | 3229.08 |  |  | 309
1980-07-27 | 3229.56 |  |  | 309
1980-07-26 | 3229.64 |  |  | 309
1980-07-25 | 3229.78 |  |  | 281
1980-07-24 | 3229.96 |  |  | 251
1980-07-23 | 3230.14 |  |  | 253
1980-07-22 | 3230.38 |  |  | 253
1980-07-21 | 3230.54 |  |  | 253
1980-07-20 | 3230.66 |  |  | 253
1980-07-19 | 3230.84 |  |  | 253
1980-07-18 | 3231 |  |  | 256
1980-07-17 | 3231.18 |  |  | 258
1980-07-16 | 3231.4 |  |  | 258
1980-07-15 | 3231.52 |  |  | 258
1980-07-14 | 3231.64 |  |  | 258
1980-07-13 | 3231.84 |  |  | 258
1980-07-12 | 3232 |  |  | 258
1980-07-11 | 3232.16 |  |  | 258
1980-07-10 | 3232.3 |  |  | 258
1980-07-09 | 3232.44 |  |  | 258
1980-07-08 | 3232.64 |  |  | 258
1980-07-07 | 3232.84 |  |  | 258
1980-07-06 | 3232.94 |  |  | 258
1980-07-05 | 3233.06 |  |  | 258
1980-07-04 | 3233.22 |  |  | 258
1980-07-03 | 3233.32 |  |  | 258
1980-07-02 | 3233.34 |  |  | 258
1980-07-01 | 3233.48 |  |  | 258
1980-06-30 | 3233.6 |  |  | 258
1980-06-29 | 3233.68 |  |  | 258
1980-06-28 | 3233.82 |  |  | 258
1980-06-27 | 3233.84 |  |  | 258
1980-06-26 | 3233.92 |  |  | 258
1980-06-25 | 3233.98 |  |  | 258
1980-06-24 | 3234.02 |  |  | 237
1980-06-23 | 3234.15 |  |  | 212
1980-06-22 | 3234.2 |  |  | 212
1980-06-21 | 3234.3 |  |  | 210
1980-06-20 | 3234.4 |  |  | 210
1980-06-19 | 3234.4 |  |  | 210
1980-06-18 | 3234.4 |  |  | 210
1980-06-17 | 3234.4 |  |  | 210
1980-06-16 | 3234.4 |  |  | 210
1980-06-15 | 3234.36 |  |  | 210
1980-06-14 | 3234.24 |  |  | 210
1980-06-13 | 3234.16 |  |  | 231
1980-06-12 | 3234.1 |  |  | 256
1980-06-11 | 3234.16 |  |  | 256
1980-06-10 | 3234.25 |  |  | 256
1980-06-09 | 3234.35 |  |  | 256
1980-06-08 | 3234.4 |  |  | 256
1980-06-07 | 3234.46 |  |  | 256
1980-06-06 | 3234.48 |  |  | 256
1980-06-05 | 3234.56 |  |  | 256
1980-06-04 | 3234.62 |  |  | 256
1980-06-03 | 3234.72 |  |  | 256
1980-06-02 | 3234.82 |  |  | 258
1980-06-01 | 3234.98 |  |  | 260
1980-05-31 | 3235.1 |  |  | 263
1980-05-30 | 3235.2 |  |  | 269
1980-05-29 | 3235.32 |  |  | 276
1980-05-28 | 3235.4 |  |  | 281
1980-05-27 | 3235.5 |  |  | 288
1980-05-26 | 3235.6 |  |  | 296
1980-05-25 | 3235.72 |  |  | 309
1980-05-24 | 3235.9 |  |  | 324
1980-05-23 | 3236.06 |  |  | 301
1980-05-22 | 3236.23 |  |  | 274
1980-05-21 | 3236.4 |  |  | 286
1980-05-20 | 3236.5 |  |  | 296
1980-05-19 | 3236.5 |  |  | 335
1980-05-18 | 3236.61 |  |  | 360
1980-05-17 | 3236.62 |  |  | 372
1980-05-16 | 3236.63 |  |  | 402
1980-05-15 | 3236.71 |  |  | 437
1980-05-14 | 3236.73 |  |  | 349
1980-05-13 | 3236.73 |  |  | 322
1980-05-12 | 3236.76 |  |  | 384
1980-05-11 | 3236.75 |  |  | 381
1980-05-10 | 3236.75 |  |  | 378
1980-05-09 | 3236.75 |  |  | 378
1980-05-08 | 3236.73 |  |  | 420
1980-05-07 | 3236.85 |  |  | 476
1980-05-06 | 3236.93 |  |  | 486
1980-05-05 | 3237.03 |  |  | 518
1980-05-04 | 3237.11 |  |  | 556
1980-05-03 | 3237.23 |  |  | 568
1980-05-02 | 3237.23 |  |  | 648
1980-05-01 | 3237.33 |  |  | 745
1980-04-30 | 3237.33 |  |  | 755
1980-04-29 | 3237.33 |  |  | 750
1980-04-28 | 3237.34 |  |  | 825
1980-04-27 | 3237.36 |  |  | 930
1980-04-26 | 3237.34 |  |  | 942
1980-04-25 | 3237.32 |  |  | 1030
1980-04-24 | 3237.3 |  |  | 1120
1980-04-23 | 3237.26 |  |  | 1250
1980-04-22 | 3237.34 |  |  | 1490
1980-04-21 | 3237.4 |  |  | 1470
1980-04-20 | 3237.4 |  |  | 1260
1980-04-19 | 3237.2 |  |  | 1230
1980-04-18 | 3236.92 |  |  | 1190
1980-04-17 | 3236.65 |  |  | 1160
1980-04-16 | 3236.48 |  |  | 1140
1980-04-15 | 3236.4 |  |  | 1240
1980-04-14 | 3236.38 |  |  | 690
1980-04-13 | 3235.92 |  |  | 291
1980-04-12 | 3235.6 |  |  | 265
1980-04-11 | 3235.4 |  |  | 208
1980-04-10 | 3235.12 |  |  | 121
1980-04-09 | 3234.78 |  |  | 114
1980-04-08 | 3234.5 |  |  | 114
1980-04-07 | 3234.28 |  |  | 114
1980-04-06 | 3234 |  |  | 112
1980-04-05 | 3233.8 |  |  | 112
1980-04-04 | 3233.55 |  |  | 160
1980-04-03 | 3233.32 |  |  | 212
1980-04-02 | 3233.15 |  |  | 212
1980-04-01 | 3232.95 |  |  | 210
1980-03-31 | 3232.85 |  |  | 210
1980-03-30 | 3232.8 |  |  | 210
1980-03-29 | 3232.6 |  |  | 210
1980-03-28 | 3232.48 |  |  | 249
1980-03-27 | 3232.34 |  |  | 293
1980-03-26 | 3232.2 |  |  | 195
1980-03-25 | 3231.98 |  |  | 140
1980-03-24 | 3231.7 |  |  | 140
1980-03-23 | 3231.42 |  |  | 140
1980-03-22 | 3231.15 |  |  | 140
1980-03-21 | 3230.8 |  |  | 140
1980-03-20 | 3230.4 |  |  | 140
1980-03-19 | 3230.12 |  |  | 139
1980-03-18 | 3229.87 |  |  | 139
1980-03-17 | 3229.55 |  |  | 139
1980-03-16 | 3229.25 |  |  | 139
1980-03-15 | 3228.9 |  |  | 139
1980-03-14 | 3228.45 |  |  | 139
1980-03-13 | 3228 |  |  | 309
1980-03-12 | 3227.55 |  |  | 542
1980-03-11 | 3227.28 |  |  | 664
1980-03-10 | 3227.1 |  |  | 840
1980-03-09 | 3227.05 |  |  | 840
1980-03-08 | 3226.95 |  |  | 840
1980-03-07 | 3226.75 |  |  | 1030
1980-03-06 | 3226.5 |  |  | 1100
1980-03-05 | 3226.25 |  |  | 1100
1980-03-04 | 3225.97 |  |  | 1270
1980-03-03 | 3225.77 |  |  | 1450
1980-03-02 | 3225.75 |  |  | 1450
1980-03-01 | 3225.7 |  |  | 1460
1980-02-29 | 3225.55 |  |  | 1450
1980-02-28 | 3225.05 |  |  | 1450
1980-02-27 | 3224 |  |  | 1280
1980-02-26 | 3221.55 |  |  | 910
1980-02-25 | 3219.65 |  |  | 1110
1980-02-24 | 3219.6 |  |  | 1120
1980-02-23 | 3219.72 |  |  | 1120
1980-02-22 | 3219.78 |  |  | 1120
1980-02-21 | 3219.65 |  |  | 1120
1980-02-20 | 3219.26 |  |  | 840
1980-02-19 | 3218.15 |  |  | 235
1980-02-18 | 3217 |  |  | 97
1980-02-17 | 3215.28 |  |  | 97
1980-02-16 | 3215 |  |  | 97
1980-02-15 | 3214.98 |  |  | 200
1980-02-14 | 3214.86 |  |  | 350
1980-02-13 | 3214.73 |  |  | 400
1980-02-12 | 3214.61 |  |  | 400
1980-02-11 | 3214.49 |  |  | 400
1980-02-10 | 3214.37 |  |  | 350
1980-02-09 | 3214.24 |  |  | 350
1980-02-08 | 3214.12 |  |  | 200
1980-02-07 | 3214 |  |  | 160
1980-02-06 | 3213.88 |  |  | 160
1980-02-05 | 3213.75 |  |  | 160
1980-02-04 | 3213.63 |  |  | 160
1980-02-03 | 3213.51 |  |  | 160
1980-02-02 | 3213.39 |  |  | 160
1980-02-01 | 3213.26 |  |  | 160
1980-01-31 | 3213.14 |  |  | 160
1980-01-30 | 3213.38 |  |  | 200
1980-01-29 | 3213.61 |  |  | 200
1980-01-28 | 3213.85 |  |  | 300
1980-01-27 | 3214.09 |  |  | 300
1980-01-26 | 3214.32 |  |  | 301
1980-01-25 | 3214.56 |  |  | 528
1980-01-24 | 3214.8 |  |  | 690
1980-01-23 | 3215.03 |  |  | 690
1980-01-22 | 3215.27 |  |  | 936
1980-01-21 | 3215.5 |  |  | 1070
1980-01-20 | 3215.74 |  |  | 1070
1980-01-19 | 3215.98 |  |  | 1070
1980-01-18 | 3216.21 |  |  | 1500
1980-01-17 | 3216.45 |  |  | 1730
1980-01-16 | 3217 |  |  | 1730
1980-01-15 | 3217.4 |  |  | 1580
1980-01-14 | 3216.85 |  |  | 1260
1980-01-13 | 3215.2 |  |  | 521
1980-01-12 | 3212.25 |  |  | 124
1980-01-11 | 3211.56 |  |  | 303
1980-01-10 | 3211.78 |  |  | 417
1980-01-09 | 3211.99 |  |  | 417
1980-01-08 | 3212.21 |  |  | 352
1980-01-07 | 3212.43 |  |  | 311
1980-01-06 | 3212.65 |  |  | 311
1980-01-05 | 3212.86 |  |  | 311
1980-01-04 | 3213.08 |  |  | 340
1980-01-03 | 3213.3 |  |  | 366
1980-01-02 | 3213.52 |  |  | 366
1980-01-01 | 3213.73 |  |  | 366
1979-12-31 | 3213.95 |  |  | 366
1979-12-30 | 3214.11 |  |  | 366
1979-12-29 | 3214.26 |  |  | 366
1979-12-28 | 3214.42 |  |  | 366
1979-12-27 | 3214.57 |  |  | 369
1979-12-26 | 3214.73 |  |  | 369
1979-12-25 | 3214.89 |  |  | 369
1979-12-24 | 3215.04 |  |  | 369
1979-12-23 | 3215.2 |  |  | 369
1979-12-22 | 3215.36 |  |  | 369
1979-12-21 | 3215.51 |  |  | 352
1979-12-20 | 3215.67 |  |  | 338
1979-12-19 | 3215.82 |  |  | 338
1979-12-18 | 3215.98 |  |  | 251
1979-12-17 | 3216.14 |  |  | 130
1979-12-16 | 3216.29 |  |  | 111
1979-12-15 | 3216.45 |  |  | 110
1979-12-14 | 3216.6 |  |  | 77
1979-12-13 | 3216.76 |  |  | 21
1979-12-12 | 3216.66 |  |  | 8
1979-12-11 | 3216.54 |  |  | 8.4
1979-12-10 | 3216.42 |  |  | 8.4
1979-12-09 | 3216.18 |  |  | 8.4
1979-12-08 | 3216.1 |  |  | 8.4
1979-12-07 | 3215.9 |  |  | 8.4
1979-12-06 | 3215.6 |  |  | 8.4
1979-12-05 | 3215.3 |  |  | 8.4
1979-12-04 | 3214.98 |  |  | 8.4
1979-12-03 | 3214.7 |  |  | 8
1979-12-02 | 3214.55 |  |  | 8
1979-12-01 | 3214.5 |  |  | 8
1979-11-30 | 3214.4 |  |  | 8
1979-11-29 | 3214.3 |  |  | 8
1979-11-28 | 3214.25 |  |  | 8
1979-11-27 | 3214.14 |  |  | 7.7
1979-11-26 | 3214.12 |  |  | 8
1979-11-25 | 3214 |  |  | 8
1979-11-24 | 3213.86 |  |  | 8.4
1979-11-23 | 3213.76 |  |  | 8
1979-11-22 | 3213.7 |  |  | 8
1979-11-21 | 3213.62 |  |  | 8
1979-11-20 | 3213.52 |  |  | 8
1979-11-19 | 3213.42 |  |  | 8.4
1979-11-18 | 3213.28 |  |  | 8
1979-11-17 | 3213.08 |  |  | 8.4
1979-11-16 | 3212.92 |  |  | 8.4
1979-11-15 | 3212.7 |  |  | 8
1979-11-14 | 3212.68 |  |  | 8
1979-11-13 | 3212.6 |  |  | 8.4
1979-11-12 | 3212.58 |  |  | 8.4
1979-11-11 | 3212.44 |  |  | 8.4
1979-11-10 | 3212.4 |  |  | 8
1979-11-09 | 3212.3 |  |  | 8.7
1979-11-08 | 3212.2 |  |  | 8.7
1979-11-07 | 3212.2 |  |  | 8.7
1979-11-06 | 3212.06 |  |  | 8.7
1979-11-05 | 3212 |  |  | 24
1979-11-04 | 3211.88 |  |  | 52
1979-11-03 | 3211.88 |  |  | 45
1979-11-02 | 3211.84 |  |  | 40
1979-11-01 | 3211.8 |  |  | 48
1979-10-31 | 3211.8 |  |  | 56
1979-10-30 | 3211.72 |  |  | 56
1979-10-29 | 3211.74 |  |  | 43
1979-10-28 | 3211.68 |  |  | 36
1979-10-27 | 3211.66 |  |  | 36
1979-10-26 | 3211.6 |  |  | 36
1979-10-25 | 3211.56 |  |  | 36
1979-10-24 | 3211.52 |  |  | 37
1979-10-23 | 3211.48 |  |  | 37
1979-10-22 | 3211.4 |  |  | 37
1979-10-21 | 3211.4 |  |  | 37
1979-10-20 | 3211.32 |  |  | 37
1979-10-19 | 3211.3 |  |  | 37
1979-10-18 | 3211.26 |  |  | 37
1979-10-17 | 3211.26 |  |  | 37
1979-10-16 | 3211.3 |  |  | 84
1979-10-15 | 3211.38 |  |  | 162
1979-10-14 | 3211.5 |  |  | 162
1979-10-13 | 3211.6 |  |  | 162
1979-10-12 | 3211.8 |  |  | 162
1979-10-11 | 3212 |  |  | 162
1979-10-10 | 3212.05 |  |  | 162
1979-10-09 | 3212.2 |  |  | 162
1979-10-08 | 3212.3 |  |  | 162
1979-10-07 | 3212.5 |  |  | 164
1979-10-06 | 3212.65 |  |  | 164
1979-10-05 | 3212.75 |  |  | 164
1979-10-04 | 3212.9 |  |  | 164
1979-10-03 | 3213 |  |  | 164
1979-10-02 | 3213.1 |  |  | 164
1979-10-01 | 3213.2 |  |  | 164
1979-09-30 | 3213.23 |  |  | 164
1979-09-29 | 3213.32 |  |  | 164
1979-09-28 | 3213.49 |  |  | 164
1979-09-27 | 3213.66 |  |  | 164
1979-09-26 | 3213.78 |  |  | 164
1979-09-25 | 3214.1 |  |  | 164
1979-09-24 | 3214.29 |  |  | 164
1979-09-23 | 3214.45 |  |  | 164
1979-09-22 | 3214.51 |  |  | 164
1979-09-21 | 3214.74 |  |  | 164
1979-09-20 | 3214.97 |  |  | 164
1979-09-19 | 3215.11 |  |  | 164
1979-09-18 | 3215.19 |  |  | 164
1979-09-17 | 3215.34 |  |  | 164
1979-09-16 | 3215.49 |  |  | 164
1979-09-15 | 3215.58 |  |  | 164
1979-09-14 | 3215.69 |  |  | 180
1979-09-13 | 3215.87 |  |  | 187
1979-09-12 | 3215.99 |  |  | 187
1979-09-11 | 3216.14 |  |  | 210
1979-09-10 | 3216.33 |  |  | 240
1979-09-09 | 3216.52 |  |  | 240
1979-09-08 | 3216.75 |  |  | 240
1979-09-07 | 3216.95 |  |  | 237
1979-09-06 | 3217.2 |  |  | 233
1979-09-05 | 3217.37 |  |  | 233
1979-09-04 | 3217.54 |  |  | 233
1979-09-03 | 3217.79 |  |  | 233
1979-09-02 | 3217.93 |  |  | 233
1979-09-01 | 3218.23 |  |  | 233
1979-08-31 | 3218.35 |  |  | 233
1979-08-30 | 3218.47 |  |  | 233
1979-08-29 | 3218.66 |  |  | 235
1979-08-28 | 3218.86 |  |  | 235
1979-08-27 | 3219.06 |  |  | 235
1979-08-26 | 3219.25 |  |  | 235
1979-08-25 | 3219.45 |  |  | 235
1979-08-24 | 3219.64 |  |  | 235
1979-08-23 | 3219.84 |  |  | 235
1979-08-22 | 3220.03 |  |  | 235
1979-08-21 | 3220.24 |  |  | 235
1979-08-20 | 3220.43 |  |  | 267
1979-08-19 | 3220.7 |  |  | 286
1979-08-18 | 3221.01 |  |  | 286
1979-08-17 | 3221.2 |  |  | 286
1979-08-16 | 3221.39 |  |  | 286
1979-08-15 | 3221.65 |  |  | 288
1979-08-14 | 3221.85 |  |  | 288
1979-08-13 | 3222.07 |  |  | 288
1979-08-12 | 3222.35 |  |  | 288
1979-08-11 | 3222.6 |  |  | 288
1979-08-10 | 3222.83 |  |  | 288
1979-08-09 | 3223.05 |  |  | 288
1979-08-08 | 3223.27 |  |  | 288
1979-08-07 | 3223.47 |  |  | 306
1979-08-06 | 3223.85 |  |  | 316
1979-08-05 | 3224.1 |  |  | 316
1979-08-04 | 3224.27 |  |  | 316
1979-08-03 | 3224.55 |  |  | 319
1979-08-02 | 3224.85 |  |  | 319
1979-08-01 | 3225.12 |  |  | 319
1979-07-31 | 3225.33 |  |  | 319
1979-07-30 | 3225.64 |  |  | 316
1979-07-29 | 3225.85 |  |  | 319
1979-07-28 | 3226.07 |  |  | 322
1979-07-27 | 3226.35 |  |  | 322
1979-07-26 | 3226.64 |  |  | 322
1979-07-25 | 3226.87 |  |  | 346
1979-07-24 | 3227.05 |  |  | 375
1979-07-23 | 3227.45 |  |  | 375
1979-07-22 | 3227.74 |  |  | 378
1979-07-21 | 3228.07 |  |  | 378
1979-07-20 | 3228.4 |  |  | 354
1979-07-19 | 3228.68 |  |  | 319
1979-07-18 | 3228.97 |  |  | 319
1979-07-17 | 3229.12 |  |  | 322
1979-07-16 | 3229.32 |  |  | 322
1979-07-15 | 3229.54 |  |  | 322
1979-07-14 | 3229.8 |  |  | 324
1979-07-13 | 3229.98 |  |  | 293
1979-07-12 | 3230.12 |  |  | 251
1979-07-11 | 3230.32 |  |  | 253
1979-07-10 | 3230.48 |  |  | 253
1979-07-09 | 3230.62 |  |  | 253
1979-07-08 | 3230.8 |  |  | 253
1979-07-07 | 3230.98 |  |  | 256
1979-07-06 | 3231.16 |  |  | 256
1979-07-05 | 3231.3 |  |  | 256
1979-07-04 | 3231.46 |  |  | 256
1979-07-03 | 3231.58 |  |  | 258
1979-07-02 | 3231.68 |  |  | 258
1979-07-01 | 3231.84 |  |  | 258
1979-06-30 | 3232.04 |  |  | 279
1979-06-29 | 3232.25 |  |  | 286
1979-06-28 | 3232.45 |  |  | 286
1979-06-27 | 3232.6 |  |  | 286
1979-06-26 | 3232.78 |  |  | 286
1979-06-25 | 3232.9 |  |  | 286
1979-06-24 | 3233.02 |  |  | 288
1979-06-23 | 3233.2 |  |  | 288
1979-06-22 | 3233.35 |  |  | 288
1979-06-21 | 3233.54 |  |  | 288
1979-06-20 | 3233.62 |  |  | 288
1979-06-19 | 3233.75 |  |  | 288
1979-06-18 | 3233.92 |  |  | 309
1979-06-17 | 3234.04 |  |  | 332
1979-06-16 | 3234.2 |  |  | 332
1979-06-15 | 3234.4 |  |  | 332
1979-06-14 | 3234.58 |  |  | 332
1979-06-13 | 3234.8 |  |  | 332
1979-06-12 | 3235.02 |  |  | 309
1979-06-11 | 3235.2 |  |  | 298
1979-06-10 | 3235.4 |  |  | 306
1979-06-09 | 3235.54 |  |  | 316
1979-06-08 | 3235.6 |  |  | 324
1979-06-07 | 3235.78 |  |  | 322
1979-06-06 | 3236 |  |  | 319
1979-06-05 | 3236.2 |  |  | 335
1979-06-04 | 3236.38 |  |  | 352
1979-06-03 | 3236.5 |  |  | 369
1979-06-02 | 3236.6 |  |  | 384
1979-06-01 | 3236.66 |  |  | 381
1979-05-31 | 3236.7 |  |  | 369
1979-05-30 | 3236.8 |  |  | 384
1979-05-29 | 3236.9 |  |  | 396
1979-05-28 | 3237.2 |  |  | 411
1979-05-27 | 3237.15 |  |  | 427
1979-05-26 | 3237.28 |  |  | 441
1979-05-25 | 3237.3 |  |  | 441
1979-05-24 | 3237.28 |  |  | 486
1979-05-23 | 3237.36 |  |  | 390
1979-05-22 | 3237.35 |  |  | 451
1979-05-21 | 3237.4 |  |  | 640
1979-05-20 | 3237.52 |  |  | 720
1979-05-19 | 3237.6 |  |  | 740
1979-05-18 | 3237.68 |  |  | 825
1979-05-17 | 3237.78 |  |  | 890
1979-05-16 | 3237.84 |  |  | 936
1979-05-15 | 3237.97 |  |  | 966
1979-05-14 | 3237.96 |  |  | 1090
1979-05-13 | 3238.1 |  |  | 1180
1979-05-12 | 3238.2 |  |  | 1200
1979-05-11 | 3238.2 |  |  | 1660
1979-05-10 | 3238.55 |  |  | 1970
1979-05-09 | 3238.7 |  |  | 2000
1979-05-08 | 3238.56 |  |  | 1960
1979-05-07 | 3238.32 |  |  | 1880
1979-05-06 | 3237.92 |  |  | 1790
1979-05-05 | 3237.02 |  |  | 1680
1979-05-04 | 3236.72 |  |  | 1670
1979-05-03 | 3236.75 |  |  | 1680
1979-05-02 | 3236.62 |  |  | 1670
1979-05-01 | 3236.4 |  |  | 1630
1979-04-30 | 3236.18 |  |  | 1610
1979-04-29 | 3236.1 |  |  | 1600
1979-04-28 | 3236.1 |  |  | 1590
1979-04-27 | 3235.98 |  |  | 1280
1979-04-26 | 3235.75 |  |  | 960
1979-04-25 | 3235.6 |  |  | 865
1979-04-24 | 3235.38 |  |  | 644
1979-04-23 | 3234.88 |  |  | 508
1979-04-22 | 3234.48 |  |  | 508
1979-04-21 | 3234.2 |  |  | 508
1979-04-20 | 3234 |  |  | 805
1979-04-19 | 3234.02 |  |  | 1180
1979-04-18 | 3234.08 |  |  | 1030
1979-04-17 | 3233.92 |  |  | 715
1979-04-16 | 3233.42 |  |  | 925
1979-04-15 | 3233.4 |  |  | 1310
1979-04-14 | 3233.45 |  |  | 1310
1979-04-13 | 3233.45 |  |  | 1310
1979-04-12 | 3233.45 |  |  | 1490
1979-04-11 | 3233.75 |  |  | 1720
1979-04-10 | 3234 |  |  | 1720
1979-04-09 | 3234.2 |  |  | 1460
1979-04-08 | 3233.98 |  |  | 1170
1979-04-07 | 3233.55 |  |  | 1160
1979-04-06 | 3233 |  |  | 1010
1979-04-05 | 3232.6 |  |  | 860
1979-04-04 | 3232.4 |  |  | 860
1979-04-03 | 3232.38 |  |  | 860
1979-04-02 | 3232.4 |  |  | 1320
1979-04-01 | 3232.75 |  |  | 1830
1979-03-31 | 3233.36 |  |  | 1910
1979-03-30 | 3233.62 |  |  | 1990
1979-03-29 | 3233.6 |  |  | 1990
1979-03-28 | 3233.2 |  |  | 1780
1979-03-27 | 3232.5 |  |  | 1500
1979-03-26 | 3231.78 |  |  | 1430
1979-03-25 | 3231.3 |  |  | 1430
1979-03-24 | 3230.68 |  |  | 1420
1979-03-23 | 3230.42 |  |  | 1360
1979-03-22 | 3230.22 |  |  | 1270
1979-03-21 | 3229.95 |  |  | 1270
1979-03-20 | 3229.65 |  |  | 1540
1979-03-19 | 3229.85 |  |  | 1950
1979-03-18 | 3230.2 |  |  | 1950
1979-03-17 | 3230.2 |  |  | 1950
1979-03-16 | 3230 |  |  | 1950
1979-03-15 | 3229.68 |  |  | 1950
1979-03-14 | 3229.6 |  |  | 1270
1979-03-13 | 3229.12 |  |  | 845
1979-03-12 | 3228.2 |  |  | 1370
1979-03-11 | 3227.85 |  |  | 1900
1979-03-10 | 3228.24 |  |  | 1940
1979-03-09 | 3228.6 |  |  | 996
1979-03-08 | 3227.98 |  |  | 2890
1979-03-07 | 3228 |  |  | 3120
1979-03-06 | 3227.18 |  |  | 2260
1979-03-05 | 3225.32 |  |  | 895
1979-03-04 | 3222.55 |  |  | 375
1979-03-03 | 3222.33 |  |  | 372
1979-03-02 | 3222.37 |  |  | 414
1979-03-01 | 3222.45 |  |  | 399
1979-02-28 | 3222.45 |  |  | 256
1979-02-27 | 3222.31 |  |  | 319
1979-02-26 | 3222.05 |  |  | 314
1979-02-25 | 3222.03 |  |  | 319
1979-02-24 | 3222.05 |  |  | 311
1979-02-23 | 3222.15 |  |  | 486
1979-02-22 | 3222.42 |  |  | 624
1979-02-21 | 3222.86 |  |  | 628
1979-02-20 | 3223.08 |  |  | 458
1979-02-19 | 3223.16 |  |  | 1060
1979-02-18 | 3223.65 |  |  | 1630
1979-02-17 | 3224.5 |  |  | 1940
1979-02-16 | 3225.42 |  |  | 2690
1979-02-15 | 3226.72 |  |  | 3140
1979-02-14 | 3228.02 |  |  | 3140
1979-02-13 | 3226.85 |  |  | 2430
1979-02-12 | 3223.64 |  |  | 948
1979-02-11 | 3219.4 |  |  | 399
1979-02-10 | 3216.18 |  |  | 393
1979-02-09 | 3213.92 |  |  | 393
1979-02-08 | 3212.4 |  |  | 227
1979-02-07 | 3212.22 |  |  | 67
1979-02-06 | 3212.03 |  |  | 67
1979-02-05 | 3211.85 |  |  | 67
1979-02-04 | 3211.67 |  |  | 63
1979-02-03 | 3211.48 |  |  | 67
1979-02-02 | 3211.3 |  |  | 84
1979-02-01 | 3211.11 |  |  | 95
1979-01-31 | 3210.93 |  |  | 133
1979-01-30 | 3210.99 |  |  | 157
1979-01-29 | 3211.05 |  |  | 155
1979-01-28 | 3211.11 |  |  | 155
1979-01-27 | 3211.17 |  |  | 157
1979-01-26 | 3211.22 |  |  | 160
1979-01-25 | 3211.28 |  |  | 250
1979-01-24 | 3211.34 |  |  | 360
1979-01-23 | 3211.4 |  |  | 390
1979-01-22 | 3211.46 |  |  | 390
1979-01-21 | 3211.82 |  |  | 510
1979-01-20 | 3211.88 |  |  | 710
1979-01-19 | 3212 |  |  | 980
1979-01-18 | 3212.38 |  |  | 910
1979-01-17 | 3212.9 |  |  | 860
1979-01-16 | 3213.46 |  |  | 800
1979-01-15 | 3213.92 |  |  | 740
1979-01-14 | 3214.14 |  |  | 400
1979-01-13 | 3214.08 |  |  | 220
1979-01-12 | 3213.5 |  |  | 120
1979-01-11 | 3213.31 |  |  | 70
1979-01-10 | 3213.13 |  |  | 69
1979-01-09 | 3212.94 |  |  | 69
1979-01-08 | 3212.75 |  |  | 69
1979-01-07 | 3212.56 |  |  | 68
1979-01-06 | 3212.38 |  |  | 68
1979-01-05 | 3212.19 |  |  | 68
1979-01-04 | 3212 |  |  | 68
1979-01-03 | 3211.81 |  |  | 68
1979-01-02 | 3211.63 |  |  | 67
1979-01-01 | 3211.44 |  |  | 67
1978-12-31 | 3211.25 |  |  | 67
1978-12-30 | 3211.24 |  |  | 67
1978-12-29 | 3211.23 |  |  | 67
1978-12-28 | 3211.22 |  |  | 67
1978-12-27 | 3211.21 |  |  | 67
1978-12-26 | 3211.2 |  |  | 67
1978-12-25 | 3211.19 |  |  | 67
1978-12-24 | 3211.18 |  |  | 67
1978-12-23 | 3211.17 |  |  | 67
1978-12-22 | 3211.16 |  |  | 85
1978-12-21 | 3211.16 |  |  | 112
1978-12-20 | 3211.16 |  |  | 112
1978-12-19 | 3211.16 |  |  | 112
1978-12-18 | 3211.24 |  |  | 112
1978-12-17 | 3211.26 |  |  | 112
1978-12-16 | 3211.26 |  |  | 112
1978-12-15 | 3211.26 |  |  | 92
1978-12-14 | 3211.24 |  |  | 65
1978-12-13 | 3211.22 |  |  | 65
1978-12-12 | 3211.2 |  |  | 65
1978-12-11 | 3211.18 |  |  | 65
1978-12-10 | 3211.1 |  |  | 65
1978-12-09 | 3211.03 |  |  | 65
1978-12-08 | 3211.03 |  |  | 78
1978-12-07 | 3211.03 |  |  | 96
1978-12-06 | 3211.03 |  |  | 96
1978-12-05 | 3211.02 |  |  | 96
1978-12-04 | 3211.02 |  |  | 206
1978-12-03 | 3211.09 |  |  | 276
1978-12-02 | 3211.25 |  |  | 279
1978-12-01 | 3211.38 |  |  | 283
1978-11-30 | 3211.56 |  |  | 628
1978-11-29 | 3212.08 |  |  | 616
1978-11-28 | 3212.48 |  |  | 298
1978-11-27 | 3212.58 |  |  | 214
1978-11-26 | 3212.56 |  |  | 119
1978-11-25 | 3212.56 |  |  | 119
1978-11-24 | 3212.7 |  |  | 119
1978-11-23 | 3212.73 |  |  | 119
1978-11-22 | 3212.77 |  |  | 119
1978-11-21 | 3212.81 |  |  | 119
1978-11-20 | 3212.85 |  |  | 121
1978-11-19 | 3212.9 |  |  | 119
1978-11-18 | 3212.9 |  |  | 118
1978-11-17 | 3212.95 |  |  | 112
1978-11-16 | 3213.02 |  |  | 122
1978-11-15 | 3213.05 |  |  | 122
1978-11-14 | 3213.1 |  |  | 83
1978-11-13 | 3213.1 |  |  | 95
1978-11-12 | 3213.19 |  |  | 119
1978-11-11 | 3213.25 |  |  | 119
1978-11-10 | 3213.35 |  |  | 118
1978-11-09 | 3213.39 |  |  | 105
1978-11-08 | 3213.43 |  |  | 98
1978-11-07 | 3213.45 |  |  | 98
1978-11-06 | 3213.47 |  |  | 96
1978-11-05 | 3213.53 |  |  | 97
1978-11-04 | 3213.55 |  |  | 96
1978-11-03 | 3213.59 |  |  | 97
1978-11-02 | 3213.63 |  |  | 97
1978-11-01 | 3213.65 |  |  | 97
1978-10-31 | 3213.65 |  |  | 128
1978-10-30 | 3213.74 |  |  | 164
1978-10-29 | 3213.86 |  |  | 164
1978-10-28 | 3213.96 |  |  | 164
1978-10-27 | 3214.06 |  |  | 191
1978-10-26 | 3214.04 |  |  | 210
1978-10-25 | 3214.43 |  |  | 208
1978-10-24 | 3214.58 |  |  | 210
1978-10-23 | 3214.78 |  |  | 210
1978-10-22 | 3214.88 |  |  | 210
1978-10-21 | 3215.04 |  |  | 208
1978-10-20 | 3215.21 |  |  | 189
1978-10-19 | 3215.3 |  |  | 180
1978-10-18 | 3215.42 |  |  | 182
1978-10-17 | 3215.5 |  |  | 180
1978-10-16 | 3215.6 |  |  | 182
1978-10-15 | 3215.65 |  |  | 180
1978-10-14 | 3215.76 |  |  | 182
1978-10-13 | 3215.91 |  |  | 180
1978-10-12 | 3216.03 |  |  | 167
1978-10-11 | 3216.16 |  |  | 180
1978-10-10 | 3216.29 |  |  | 180
1978-10-09 | 3216.39 |  |  | 180
1978-10-08 | 3216.5 |  |  | 180
1978-10-07 | 3216.59 |  |  | 180
1978-10-06 | 3216.69 |  |  | 178
1978-10-05 | 3216.79 |  |  | 178
1978-10-04 | 3216.91 |  |  | 178
1978-10-03 | 3217.02 |  |  | 178
1978-10-02 | 3217.19 |  |  | 178
1978-10-01 | 3217.29 |  |  | 178
1978-09-30 | 3217.4 |  |  | 178
1978-09-29 | 3217.54 |  |  | 178
1978-09-28 | 3217.8 |  |  | 178
1978-09-27 | 3217.84 |  |  | 178
1978-09-26 | 3217.96 |  |  | 178
1978-09-25 | 3218.09 |  |  | 178
1978-09-24 | 3218.2 |  |  | 178
1978-09-23 | 3218.27 |  |  | 178
1978-09-22 | 3218.31 |  |  | 195
1978-09-21 | 3218.43 |  |  | 206
1978-09-20 | 3218.57 |  |  | 206
1978-09-19 | 3218.7 |  |  | 206
1978-09-18 | 3218.84 |  |  | 206
1978-09-17 | 3219 |  |  | 206
1978-09-16 | 3219.16 |  |  | 206
1978-09-15 | 3219.31 |  |  | 206
1978-09-14 | 3219.46 |  |  | 206
1978-09-13 | 3219.57 |  |  | 206
1978-09-12 | 3219.71 |  |  | 206
1978-09-11 | 3219.86 |  |  | 206
1978-09-10 | 3219.98 |  |  | 206
1978-09-09 | 3220.14 |  |  | 206
1978-09-08 | 3220.36 |  |  | 218
1978-09-07 | 3220.49 |  |  | 229
1978-09-06 | 3220.75 |  |  | 229
1978-09-05 | 3221 |  |  | 229
1978-09-04 | 3222.25 |  |  | 229
1978-09-03 | 3222.58 |  |  | 231
1978-09-02 | 3222.38 |  |  | 231
1978-09-01 | 3222.22 |  |  | 231
1978-08-31 | 3222.08 |  |  | 231
1978-08-30 | 3221.9 |  |  | 231
1978-08-29 | 3222.1 |  |  | 231
1978-08-28 | 3222.3 |  |  | 231
1978-08-27 | 3222.48 |  |  | 231
1978-08-26 | 3222.63 |  |  | 231
1978-08-25 | 3222.8 |  |  | 231
1978-08-24 | 3222.97 |  |  | 233
1978-08-23 | 3223.15 |  |  | 233
1978-08-22 | 3223.3 |  |  | 233
1978-08-21 | 3223.53 |  |  | 233
1978-08-20 | 3223.75 |  |  | 233
1978-08-19 | 3223.93 |  |  | 233
1978-08-18 | 3224.1 |  |  | 244
1978-08-17 | 3224.23 |  |  | 258
1978-08-16 | 3224.44 |  |  | 260
1978-08-15 | 3224.7 |  |  | 260
1978-08-14 | 3224.86 |  |  | 260
1978-08-13 | 3225.04 |  |  | 260
1978-08-12 | 3225.25 |  |  | 260
1978-08-11 | 3225.5 |  |  | 260
1978-08-10 | 3225.9 |  |  | 260
1978-08-09 | 3225.96 |  |  | 263
1978-08-08 | 3226.18 |  |  | 263
1978-08-07 | 3226.37 |  |  | 263
1978-08-06 | 3226.54 |  |  | 263
1978-08-05 | 3226.8 |  |  | 263
1978-08-04 | 3227 |  |  | 263
1978-08-03 | 3227.23 |  |  | 263
1978-08-02 | 3227.34 |  |  | 263
1978-08-01 | 3227.58 |  |  | 265
1978-07-31 | 3227.76 |  |  | 265
1978-07-30 | 3227.98 |  |  | 265
1978-07-29 | 3228.17 |  |  | 265
1978-07-28 | 3228.36 |  |  | 267
1978-07-27 | 3228.54 |  |  | 267
1978-07-26 | 3228.7 |  |  | 267
1978-07-25 | 3228.92 |  |  | 267
1978-07-24 | 3229.14 |  |  | 298
1978-07-23 | 3229.39 |  |  | 314
1978-07-22 | 3229.6 |  |  | 314
1978-07-21 | 3229.8 |  |  | 314
1978-07-20 | 3230 |  |  | 316
1978-07-19 | 3230.2 |  |  | 316
1978-07-18 | 3230.2 |  |  | 316
1978-07-17 | 3230.54 |  |  | 260
1978-07-16 | 3230.64 |  |  | 224
1978-07-15 | 3230.79 |  |  | 224
1978-07-14 | 3230.93 |  |  | 224
1978-07-13 | 3231.05 |  |  | 226
1978-07-12 | 3231.14 |  |  | 226
1978-07-11 | 3231.22 |  |  | 227
1978-07-10 | 3231.34 |  |  | 227
1978-07-09 | 3231.42 |  |  | 229
1978-07-08 | 3231.53 |  |  | 229
1978-07-07 | 3231.6 |  |  | 229
1978-07-06 | 3231.7 |  |  | 231
1978-07-05 | 3231.76 |  |  | 231
1978-07-04 | 3231.85 |  |  | 233
1978-07-03 | 3231.92 |  |  | 233
1978-07-02 | 3232.02 |  |  | 233
1978-07-01 | 3232.15 |  |  | 235
1978-06-30 | 3232.2 |  |  | 235
1978-06-29 | 3232.27 |  |  | 235
1978-06-28 | 3232.37 |  |  | 235
1978-06-27 | 3232.47 |  |  | 235
1978-06-26 | 3232.56 |  |  | 235
1978-06-25 | 3232.63 |  |  | 237
1978-06-24 | 3232.72 |  |  | 237
1978-06-23 | 3232.71 |  |  | 237
1978-06-22 | 3232.87 |  |  | 237
1978-06-21 | 3232.94 |  |  | 235
1978-06-20 | 3233.23 |  |  | 237
1978-06-19 | 3233.25 |  |  | 237
1978-06-18 | 3233.53 |  |  | 237
1978-06-17 | 3233.51 |  |  | 235
1978-06-16 | 3233.54 |  |  | 235
1978-06-15 | 3233.58 |  |  | 235
1978-06-14 | 3233.67 |  |  | 235
1978-06-13 | 3233.82 |  |  | 235
1978-06-12 | 3233.92 |  |  | 235
1978-06-11 | 3234 |  |  | 233
1978-06-10 | 3234.35 |  |  | 233
1978-06-09 | 3234.14 |  |  | 242
1978-06-08 | 3234.29 |  |  | 246
1978-06-07 | 3234.42 |  |  | 244
1978-06-06 | 3234.52 |  |  | 244
1978-06-05 | 3234.59 |  |  | 244
1978-06-04 | 3234.68 |  |  | 242
1978-06-03 | 3234.75 |  |  | 242
1978-06-02 | 3234.78 |  |  | 251
1978-06-01 | 3234.86 |  |  | 258
1978-05-31 | 3234.86 |  |  | 274
1978-05-30 | 3234.94 |  |  | 298
1978-05-29 | 3234.99 |  |  | 298
1978-05-28 | 3234.99 |  |  | 301
1978-05-27 | 3234.98 |  |  | 301
1978-05-26 | 3234.98 |  |  | 301
1978-05-25 | 3235 |  |  | 298
1978-05-24 | 3234.97 |  |  | 237
1978-05-23 | 3234.95 |  |  | 490
1978-05-22 | 3234.79 |  |  | 560
1978-05-21 | 3235.55 |  |  | 572
1978-05-20 | 3235.98 |  |  | 580
1978-05-19 | 3235.48 |  |  | 588
1978-05-18 | 3235.57 |  |  | 596
1978-05-17 | 3235.58 |  |  | 600
1978-05-16 | 3235.59 |  |  | 539
1978-05-15 | 3235.51 |  |  | 393
1978-05-14 | 3235.42 |  |  | 301
1978-05-13 | 3235.3 |  |  | 286
1978-05-12 | 3235.11 |  |  | 281
1978-05-11 | 3234.94 |  |  | 272
1978-05-10 | 3234.73 |  |  | 267
1978-05-09 | 3234.53 |  |  | 750
1978-05-08 | 3234.73 |  |  | 1150
1978-05-07 | 3235.1 |  |  | 1170
1978-05-06 | 3235.44 |  |  | 1200
1978-05-05 | 3235.91 |  |  | 1350
1978-05-04 | 3236.3 |  |  | 1470
1978-05-03 | 3236.56 |  |  | 1530
1978-05-02 | 3236.98 |  |  | 1590
1978-05-01 | 3237.37 |  |  | 1630
1978-04-30 | 3237.61 |  |  | 1670
1978-04-29 | 3237.77 |  |  | 1690
1978-04-28 | 3237.73 |  |  | 1560
1978-04-27 | 3237.3 |  |  | 1380
1978-04-26 | 3236.01 |  |  | 895
1978-04-25 | 3235.11 |  |  | 430
1978-04-24 | 3235.01 |  |  | 535
1978-04-23 | 3235.11 |  |  | 668
1978-04-22 | 3235.31 |  |  | 676
1978-04-21 | 3235.33 |  |  | 680
1978-04-20 | 3235.43 |  |  | 690
1978-04-19 | 3235.45 |  |  | 690
1978-04-18 | 3235.38 |  |  | 695
1978-04-17 | 3235.31 |  |  | 690
1978-04-16 | 3235.33 |  |  | 690
1978-04-15 | 3235.37 |  |  | 685
1978-04-14 | 3235.4 |  |  | 680
1978-04-13 | 3235.34 |  |  | 830
1978-04-12 | 3235.38 |  |  | 936
1978-04-11 | 3235.35 |  |  | 845
1978-04-10 | 3235.44 |  |  | 664
1978-04-09 | 3235.22 |  |  | 584
1978-04-08 | 3234.96 |  |  | 572
1978-04-07 | 3234.61 |  |  | 705
1978-04-06 | 3234.28 |  |  | 936
1978-04-05 | 3234.1 |  |  | 1390
1978-04-04 | 3234.21 |  |  | 1820
1978-04-03 | 3234.38 |  |  | 1940
1978-04-02 | 3234.38 |  |  | 1880
1978-04-01 | 3234 |  |  | 1870
1978-03-31 | 3233.6 |  |  | 1760
1978-03-30 | 3233.34 |  |  | 1550
1978-03-29 | 3233.06 |  |  | 1420
1978-03-28 | 3232.66 |  |  | 1240
1978-03-27 | 3232.23 |  |  | 1170
1978-03-26 | 3231.6 |  |  | 1230
1978-03-25 | 3231.02 |  |  | 1580
1978-03-24 | 3230.57 |  |  | 1610
1978-03-23 | 3229.96 |  |  | 870
1978-03-22 | 3228.86 |  |  | 549
1978-03-21 | 3227.56 |  |  | 546
1978-03-20 | 3226.38 |  |  | 542
1978-03-19 | 3225.15 |  |  | 542
1978-03-18 | 3223.98 |  |  | 539
1978-03-17 | 3222.99 |  |  | 539
1978-03-16 | 3222.99 |  |  | 539
1978-03-15 | 3222.71 |  |  | 740
1978-03-14 | 3222.64 |  |  | 1390
1978-03-13 | 3222.95 |  |  | 1810
1978-03-12 | 3223.21 |  |  | 1810
1978-03-11 | 3223.33 |  |  | 1810
1978-03-10 | 3223.41 |  |  | 1480
1978-03-09 | 3222.49 |  |  | 960
1978-03-08 | 3220.24 |  |  | 745
1978-03-07 | 3219.21 |  |  | 740
1978-03-06 | 3218.87 |  |  | 656
1978-03-05 | 3218.23 |  |  | 564
1978-03-04 | 3217.94 |  |  | 564
1978-03-03 | 3217.91 |  |  | 455
1978-03-02 | 3217.65 |  |  | 381
1978-03-01 | 3217.46 |  |  | 381
1978-02-28 | 3217.17 |  |  | 316
1978-02-27 | 3216.67 |  |  | 246
1978-02-26 | 3215.96 |  |  | 246
1978-02-25 | 3216.01 |  |  | 246
1978-02-24 | 3214.16 |  |  | 246
1978-02-23 | 3213.5 |  |  | 244
1978-02-22 | 3212.82 |  |  | 244
1978-02-21 | 3212.16 |  |  | 244
1978-02-20 | 3211.68 |  |  | 244
1978-02-19 | 3211.44 |  |  | 244
1978-02-18 | 3211.36 |  |  | 244
1978-02-17 | 3211.28 |  |  | 369
1978-02-16 | 3211.36 |  |  | 514
1978-02-15 | 3211.49 |  |  | 518
1978-02-14 | 3211.51 |  |  | 518
1978-02-13 | 3211.52 |  |  | 518
1978-02-12 | 3211.53 |  |  | 518
1978-02-11 | 3211.54 |  |  | 1050
1978-02-10 | 3212.12 |  |  | 1600
1978-02-09 | 3212.79 |  |  | 1600
1978-02-08 | 3213.38 |  |  | 1610
1978-02-07 | 3213.73 |  |  | 1320
1978-02-06 | 3213.73 |  |  | 685
1978-02-05 | 3213.18 |  |  | 375
1978-02-04 | 3212.45 |  |  | 375
1978-02-03 | 3211.32 |  |  | 372
1978-02-02 | 3211.03 |  |  | 372
1978-02-01 | 3211.07 |  |  | 372
1978-01-31 | 3210.98 |  |  | 372
1978-01-30 | 3211.07 |  |  | 372
1978-01-29 | 3211.07 |  |  | 372
1978-01-28 | 3211.07 |  |  | 372
1978-01-27 | 3211.07 |  |  | 301
1978-01-26 | 3210.93 |  |  | 249
1978-01-25 | 3210.7 |  |  | 309
1978-01-24 | 3210.58 |  |  | 672
1978-01-23 | 3210.83 |  |  | 1020
1978-01-22 | 3211.16 |  |  | 1190
1978-01-21 | 3211.58 |  |  | 1190
1978-01-20 | 3211.57 |  |  | 1150
1978-01-19 | 3211.53 |  |  | 765
1978-01-18 | 3211.19 |  |  | 298
1978-01-17 | 3210.23 |  |  | 105
1978-01-16 | 3208.55 |  |  | 60
1978-01-15 | 3206.71 |  |  | 57
1978-01-14 | 3204.43 |  |  | 57
1978-01-13 | 3203.51 |  |  | 56
1978-01-12 | 3202.84 |  |  | 56
1978-01-11 | 3202.03 |  |  | 51
1978-01-10 | 3200.63 |  |  | 48
1978-01-09 | 3199.42 |  |  | 48
1978-01-08 | 3199.05 |  |  | 48
1978-01-07 | 3198.77 |  |  | 48
1978-01-06 | 3198.54 |  |  | 48
1978-01-05 | 3197.99 |  |  | 47
1978-01-04 | 3197.94 |  |  | 47
1978-01-03 | 3197.73 |  |  | 47
1978-01-02 | 3197.53 |  |  | 47
1978-01-01 | 3197.46 |  |  | 47
1977-12-31 | 3197.34 |  |  | 47
1977-12-30 | 3197.02 |  |  | 47
1977-12-29 | 3196.8 |  |  | 47
1977-12-28 | 3196.51 |  |  | 47
1977-12-27 | 3196.21 |  |  | 47
1977-12-26 | 3195.9 |  |  | 47
1977-12-25 | 3195.53 |  |  | 47
1977-12-24 | 3195.17 |  |  | 47
1977-12-23 | 3194.76 |  |  | 47
1977-12-22 | 3194.39 |  |  | 47
1977-12-21 | 3194.12 |  |  | 47
1977-12-20 | 3194.25 |  |  | 47
1977-12-19 | 3194.11 |  |  | 32
1977-12-18 | 3193.75 |  |  | 24
1977-12-17 | 3192.93 |  |  | 24
1977-12-16 | 3192 |  |  | 23
1977-12-15 | 3189.5 |  |  | 23
1977-12-14 | 3184.95 |  |  | 22
1977-12-13 | 3183.51 |  |  | 22
1977-12-12 | 3183.35 |  |  | 22
1977-12-11 | 3183.23 |  |  | 22
1977-12-10 | 3183.07 |  |  | 22
1977-12-09 | 3182.95 |  |  | 22
1977-12-08 | 3182.75 |  |  | 22
1977-12-07 | 3182.55 |  |  | 22
1977-12-06 | 3182.36 |  |  | 22
1977-12-05 | 3182.11 |  |  | 22
1977-12-04 | 3181.85 |  |  | 22
1977-12-03 | 3181.16 |  |  | 22
1977-12-02 | 3181.1 |  |  | 22
1977-12-01 | 3180.9 |  |  | 22
1977-11-30 | 3180.6 |  |  | 22
1977-11-29 | 3180.25 |  |  | 22
1977-11-28 | 3179.97 |  |  | 22
1977-11-27 | 3179.43 |  |  | 22
1977-11-26 | 3178.92 |  |  | 22
1977-11-25 | 3178.59 |  |  | 22
1977-11-24 | 3178.45 |  |  | 22
1977-11-23 | 3178.32 |  |  | 22
1977-11-22 | 3178.23 |  |  | 22
1977-11-21 | 3178.19 |  |  | 22
1977-11-20 | 3178.15 |  |  | 21
1977-11-19 | 3178.15 |  |  | 21
1977-11-18 | 3178.12 |  |  | 20
1977-11-17 | 3178.08 |  |  | 26
1977-11-16 | 3178.03 |  |  | 26
1977-11-15 | 3178 |  |  | 26
1977-11-14 | 3177.95 |  |  | 26
1977-11-13 | 3177.92 |  |  | 26
1977-11-12 | 3177.85 |  |  | 26
1977-11-11 | 3177.83 |  |  | 26
1977-11-10 | 3177.79 |  |  | 26
1977-11-09 | 3177.75 |  |  | 26
1977-11-08 | 3177.7 |  |  | 26
1977-11-07 | 3177.65 |  |  | 26
1977-11-06 | 3177.6 |  |  | 26
1977-11-05 | 3177.55 |  |  | 26
1977-11-04 | 3177.55 |  |  | 26
1977-11-03 | 3177.45 |  |  | 26
1977-11-02 | 3177.43 |  |  | 26
1977-11-01 | 3177.42 |  |  | 38
1977-10-31 | 3177.4 |  |  | 61
1977-10-30 | 3177.4 |  |  | 60
1977-10-29 | 3177.41 |  |  | 60
1977-10-28 | 3177.41 |  |  | 60
1977-10-27 | 3177.41 |  |  | 60
1977-10-26 | 3177.41 |  |  | 60
1977-10-25 | 3177.42 |  |  | 60
1977-10-24 | 3177.42 |  |  | 60
1977-10-23 | 3177.42 |  |  | 60
1977-10-22 | 3177.42 |  |  | 60
1977-10-21 | 3177.43 |  |  | 60
1977-10-20 | 3177.43 |  |  | 60
1977-10-19 | 3177.43 |  |  | 60
1977-10-18 | 3177.43 |  |  | 60
1977-10-17 | 3177.44 |  |  | 60
1977-10-16 | 3177.44 |  |  | 60
1977-10-15 | 3177.44 |  |  | 60
1977-10-14 | 3177.43 |  |  | 61
1977-10-13 | 3177.52 |  |  | 60
1977-10-12 | 3177.58 |  |  | 60
1977-10-11 | 3177.61 |  |  | 60
1977-10-10 | 3177.65 |  |  | 60
1977-10-09 | 3177.66 |  |  | 60
1977-10-08 | 3177.82 |  |  | 60
1977-10-07 | 3177.85 |  |  | 60
1977-10-06 | 3177.78 |  |  | 60
1977-10-05 | 3177.77 |  |  | 60
1977-10-04 | 3177.83 |  |  | 60
1977-10-03 | 3177.83 |  |  | 60
1977-10-02 | 3177.86 |  |  | 62
1977-10-01 | 3177.91 |  |  | 68
1977-09-30 | 3178 |  |  | 66
1977-09-29 | 3178.06 |  |  | 85
1977-09-28 | 3178.15 |  |  | 110
1977-09-27 | 3178.24 |  |  | 140
1977-09-26 | 3178.41 |  |  | 151
1977-09-25 | 3178.7 |  |  | 152
1977-09-24 | 3178.9 |  |  | 162
1977-09-23 | 3179.14 |  |  | 174
1977-09-22 | 3179.42 |  |  | 208
1977-09-21 | 3179.72 |  |  | 231
1977-09-20 | 3180.02 |  |  | 227
1977-09-19 | 3180.3 |  |  | 220
1977-09-18 | 3180.55 |  |  | 240
1977-09-17 | 3180.88 |  |  | 242
1977-09-16 | 3181.22 |  |  | 242
1977-09-15 | 3181.55 |  |  | 244
1977-09-14 | 3182 |  |  | 244
1977-09-13 | 3182.5 |  |  | 244
1977-09-12 | 3182.78 |  |  | 229
1977-09-11 | 3183.1 |  |  | 218
1977-09-10 | 3183.34 |  |  | 218
1977-09-09 | 3183.65 |  |  | 218
1977-09-08 | 3183.9 |  |  | 218
1977-09-07 | 3184 |  |  | 218
1977-09-06 | 3184.46 |  |  | 218
1977-09-05 | 3184.8 |  |  | 220
1977-09-04 | 3185.17 |  |  | 220
1977-09-03 | 3185.24 |  |  | 220
1977-09-02 | 3185.66 |  |  | 251
1977-09-01 | 3185.98 |  |  | 244
1977-08-31 | 3186.16 |  |  | 244
1977-08-30 | 3186.6 |  |  | 256
1977-08-29 | 3186.9 |  |  | 272
1977-08-28 | 3187.3 |  |  | 274
1977-08-27 | 3187.66 |  |  | 279
1977-08-26 | 3188.11 |  |  | 286
1977-08-25 | 3188.32 |  |  | 298
1977-08-24 | 3188.82 |  |  | 298
1977-08-23 | 3189.17 |  |  | 298
1977-08-22 | 3189.34 |  |  | 301
1977-08-21 | 3189.92 |  |  | 303
1977-08-20 | 3190.34 |  |  | 303
1977-08-19 | 3190.75 |  |  | 303
1977-08-18 | 3191.11 |  |  | 303
1977-08-17 | 3191.46 |  |  | 303
1977-08-16 | 3191.92 |  |  | 303
1977-08-15 | 3192.21 |  |  | 303
1977-08-14 | 3192.6 |  |  | 303
1977-08-13 | 3192.94 |  |  | 303
1977-08-12 | 3193.37 |  |  | 316
1977-08-11 | 3193.74 |  |  | 332
1977-08-10 | 3194.21 |  |  | 332
1977-08-09 | 3194.61 |  |  | 332
1977-08-08 | 3194.96 |  |  | 332
1977-08-07 | 3195.3 |  |  | 332
1977-08-06 | 3195.72 |  |  | 332
1977-08-05 | 3196.1 |  |  | 332
1977-08-04 | 3196.35 |  |  | 332
1977-08-03 | 3196.97 |  |  | 338
1977-08-02 | 3197.41 |  |  | 340
1977-08-01 | 3197.77 |  |  | 316
1977-07-31 | 3198.06 |  |  | 314
1977-07-30 | 3198.43 |  |  | 314
1977-07-29 | 3198.78 |  |  | 314
1977-07-28 | 3199.16 |  |  | 314
1977-07-27 | 3199.63 |  |  | 316
1977-07-26 | 3199.9 |  |  | 316
1977-07-25 | 3200.3 |  |  | 329
1977-07-24 | 3200.6 |  |  | 346
1977-07-23 | 3201.1 |  |  | 346
1977-07-22 | 3201.3 |  |  | 338
1977-07-21 | 3201.72 |  |  | 329
1977-07-20 | 3202.12 |  |  | 329
1977-07-19 | 3202.45 |  |  | 329
1977-07-18 | 3202.78 |  |  | 332
1977-07-17 | 3203.16 |  |  | 332
1977-07-16 | 3203.48 |  |  | 332
1977-07-15 | 3203.8 |  |  | 327
1977-07-14 | 3204.2 |  |  | 319
1977-07-13 | 3204.52 |  |  | 319
1977-07-12 | 3204.92 |  |  | 319
1977-07-11 | 3205.28 |  |  | 322
1977-07-10 | 3205.5 |  |  | 322
1977-07-09 | 3205.82 |  |  | 322
1977-07-08 | 3206.19 |  |  | 322
1977-07-07 | 3206.48 |  |  | 314
1977-07-06 | 3206.78 |  |  | 235
1977-07-05 | 3207 |  |  | 193
1977-07-04 | 3207.22 |  |  | 193
1977-07-03 | 3207.45 |  |  | 193
1977-07-02 | 3207.7 |  |  | 193
1977-07-01 | 3207.95 |  |  | 193
1977-06-30 | 3208.2 |  |  | 193
1977-06-29 | 3208.35 |  |  | 193
1977-06-28 | 3208.55 |  |  | 193
1977-06-27 | 3208.72 |  |  | 199
1977-06-26 | 3208.9 |  |  | 205
1977-06-25 | 3209.1 |  |  | 205
1977-06-24 | 3209.32 |  |  | 203
1977-06-23 | 3209.52 |  |  | 203
1977-06-22 | 3209.72 |  |  | 203
1977-06-21 | 3209.93 |  |  | 203
1977-06-20 | 3210.1 |  |  | 203
1977-06-19 | 3210.35 |  |  | 240
1977-06-18 | 3210.65 |  |  | 309
1977-06-17 | 3210.98 |  |  | 340
1977-06-16 | 3211.2 |  |  | 378
1977-06-15 | 3211.54 |  |  | 378
1977-06-14 | 3211.88 |  |  | 378
1977-06-13 | 3212.2 |  |  | 363
1977-06-12 | 3212.48 |  |  | 340
1977-06-11 | 3212.75 |  |  | 340
1977-06-10 | 3213 |  |  | 340
1977-06-09 | 3213.25 |  |  | 340
1977-06-08 | 3213.52 |  |  | 340
1977-06-07 | 3213.79 |  |  | 340
1977-06-06 | 3214.04 |  |  | 340
1977-06-05 | 3214.32 |  |  | 343
1977-06-04 | 3214.53 |  |  | 343
1977-06-03 | 3214.8 |  |  | 338
1977-06-02 | 3215.07 |  |  | 327
1977-06-01 | 3215.35 |  |  | 306
1977-05-31 | 3215.61 |  |  | 251
1977-05-30 | 3215.81 |  |  | 226
1977-05-29 | 3215.91 |  |  | 226
1977-05-28 | 3215.91 |  |  | 176
1977-05-27 | 3215.84 |  |  | 103
1977-05-26 | 3215.84 |  |  | 103
1977-05-25 | 3215.83 |  |  | 103
1977-05-24 | 3215.81 |  |  | 103
1977-05-23 | 3215.78 |  |  | 103
1977-05-22 | 3215.78 |  |  | 103
1977-05-21 | 3215.77 |  |  | 103
1977-05-20 | 3215.77 |  |  | 89
1977-05-19 | 3215.64 |  |  | 79
1977-05-18 | 3215.59 |  |  | 79
1977-05-17 | 3215.5 |  |  | 79
1977-05-16 | 3215.37 |  |  | 79
1977-05-15 | 3215.22 |  |  | 79
1977-05-14 | 3215.06 |  |  | 79
1977-05-13 | 3214.74 |  |  | 79
1977-05-12 | 3214.27 |  |  | 78
1977-05-11 | 3213.33 |  |  | 78
1977-05-10 | 3213.13 |  |  | 118
1977-05-09 | 3213.23 |  |  | 165
1977-05-08 | 3213.24 |  |  | 165
1977-05-07 | 3213.35 |  |  | 165
1977-05-06 | 3213.35 |  |  | 173
1977-05-05 | 3213.44 |  |  | 176
1977-05-04 | 3213.56 |  |  | 176
1977-05-03 | 3213.72 |  |  | 176
1977-05-02 | 3213.84 |  |  | 189
1977-05-01 | 3213.88 |  |  | 203
1977-04-30 | 3214.03 |  |  | 203
1977-04-29 | 3214.18 |  |  | 203
1977-04-28 | 3214.35 |  |  | 203
1977-04-27 | 3214.46 |  |  | 171
1977-04-26 | 3214.6 |  |  | 160
1977-04-25 | 3214.69 |  |  | 160
1977-04-24 | 3214.86 |  |  | 158
1977-04-23 | 3214.91 |  |  | 158
1977-04-22 | 3215.04 |  |  | 158
1977-04-21 | 3215.15 |  |  | 158
1977-04-20 | 3215.15 |  |  | 158
1977-04-19 | 3215.25 |  |  | 158
1977-04-18 | 3215.34 |  |  | 158
1977-04-17 | 3215.4 |  |  | 158
1977-04-16 | 3215.46 |  |  | 158
1977-04-15 | 3215.46 |  |  | 146
1977-04-14 | 3215.42 |  |  | 139
1977-04-13 | 3215.41 |  |  | 140
1977-04-12 | 3215.4 |  |  | 114
1977-04-11 | 3215.34 |  |  | 98
1977-04-10 | 3215.32 |  |  | 98
1977-04-09 | 3215.24 |  |  | 114
1977-04-08 | 3215.16 |  |  | 68
1977-04-07 | 3214.93 |  |  | 35
1977-04-06 | 3214.72 |  |  | 35
1977-04-05 | 3214.61 |  |  | 35
1977-04-04 | 3214.51 |  |  | 35
1977-04-03 | 3214.41 |  |  | 35
1977-04-02 | 3214.35 |  |  | 34
1977-04-01 | 3214.33 |  |  | 34
1977-03-31 | 3214.33 |  |  | 35
1977-03-30 | 3214.25 |  |  | 35
1977-03-29 | 3214.22 |  |  | 34
1977-03-28 | 3214.14 |  |  | 35
1977-03-27 | 3214.13 |  |  | 35
1977-03-26 | 3214.07 |  |  | 35
1977-03-25 | 3214.02 |  |  | 35
1977-03-24 | 3213.92 |  |  | 35
1977-03-23 | 3213.9 |  |  | 35
1977-03-22 | 3213.84 |  |  | 35
1977-03-21 | 3213.8 |  |  | 35
1977-03-20 | 3213.76 |  |  | 35
1977-03-19 | 3213.74 |  |  | 35
1977-03-18 | 3213.61 |  |  | 35
1977-03-17 | 3213.58 |  |  | 35
1977-03-16 | 3213.53 |  |  | 34
1977-03-15 | 3213.51 |  |  | 34
1977-03-14 | 3213.48 |  |  | 34
1977-03-13 | 3213.41 |  |  | 34
1977-03-12 | 3213.38 |  |  | 34
1977-03-11 | 3213.31 |  |  | 34
1977-03-10 | 3213.24 |  |  | 34
1977-03-09 | 3213.15 |  |  | 34
1977-03-08 | 3213.08 |  |  | 34
1977-03-07 | 3213.05 |  |  | 34
1977-03-06 | 3213 |  |  | 34
1977-03-05 | 3213 |  |  | 34
1977-03-04 | 3212.9 |  |  | 34
1977-03-03 | 3212.87 |  |  | 35
1977-03-02 | 3212.77 |  |  | 35
1977-03-01 | 3212.75 |  |  | 35
1977-02-28 | 3212.73 |  |  | 35
1977-02-27 | 3212.57 |  |  | 35
1977-02-26 | 3212.55 |  |  | 35
1977-02-25 | 3212.53 |  |  | 35
1977-02-24 | 3212.47 |  |  | 35
1977-02-23 | 3212.45 |  |  | 35
1977-02-22 | 3212.43 |  |  | 34
1977-02-21 | 3212.36 |  |  | 34
1977-02-20 | 3212.33 |  |  | 34
1977-02-19 | 3212.25 |  |  | 34
1977-02-18 | 3212.17 |  |  | 34
1977-02-17 | 3212.15 |  |  | 34
1977-02-16 | 3212.07 |  |  | 34
1977-02-15 | 3212 |  |  | 34
1977-02-14 | 3211.95 |  |  | 34
1977-02-13 | 3211.87 |  |  | 34
1977-02-12 | 3211.8 |  |  | 34
1977-02-11 | 3211.75 |  |  | 34
1977-02-10 | 3211.73 |  |  | 34
1977-02-09 | 3211.65 |  |  | 34
1977-02-08 | 3211.57 |  |  | 34
1977-02-07 | 3211.54 |  |  | 34
1977-02-06 | 3211.47 |  |  | 34
1977-02-05 | 3211.45 |  |  | 34
1977-02-04 | 3211.4 |  |  | 34
1977-02-03 | 3211.37 |  |  | 33
1977-02-02 | 3211.35 |  |  | 34
1977-02-01 | 3211.33 |  |  | 34
1977-01-31 | 3211.3 |  |  | 38
1977-01-30 | 3211.27 |  |  | 42
1977-01-29 | 3211.25 |  |  | 42
1977-01-28 | 3211.25 |  |  | 39
1977-01-27 | 3211.23 |  |  | 38
1977-01-26 | 3211.23 |  |  | 38
1977-01-25 | 3211.2 |  |  | 38
1977-01-24 | 3211.15 |  |  | 38
1977-01-23 | 3211.1 |  |  | 38
1977-01-22 | 3211.05 |  |  | 38
1977-01-21 | 3211.03 |  |  | 38
1977-01-20 | 3211 |  |  | 52
1977-01-19 | 3210.96 |  |  | 62
1977-01-18 | 3210.95 |  |  | 62
1977-01-17 | 3210.95 |  |  | 62
1977-01-16 | 3210.95 |  |  | 62
1977-01-15 | 3210.95 |  |  | 61
1977-01-14 | 3210.95 |  |  | 61
1977-01-13 | 3210.95 |  |  | 61
1977-01-12 | 3210.96 |  |  | 61
1977-01-11 | 3210.96 |  |  | 61
1977-01-10 | 3210.96 |  |  | 61
1977-01-09 | 3211 |  |  | 61
1977-01-08 | 3211.02 |  |  | 61
1977-01-07 | 3211.03 |  |  | 61
1977-01-06 | 3211.07 |  |  | 61
1977-01-05 | 3211.09 |  |  | 61
1977-01-04 | 3211.1 |  |  | 62
1977-01-03 | 3211.1 |  |  | 62
1977-01-02 | 3211.1 |  |  | 62
1977-01-01 | 3211.1 |  |  | 62
1976-12-31 | 3211.1 |  |  | 63
1976-12-30 | 3211.1 |  |  | 64
1976-12-29 | 3211.1 |  |  | 63
1976-12-28 | 3211.1 |  |  | 63
1976-12-27 | 3211.1 |  |  | 75
1976-12-26 | 3211.1 |  |  | 88
1976-12-25 | 3211.15 |  |  | 88
1976-12-24 | 3211.17 |  |  | 88
1976-12-23 | 3211.18 |  |  | 89
1976-12-22 | 3211.2 |  |  | 89
1976-12-21 | 3211.2 |  |  | 89
1976-12-20 | 3211.21 |  |  | 89
1976-12-19 | 3211.28 |  |  | 88
1976-12-18 | 3211.3 |  |  | 86
1976-12-17 | 3211.3 |  |  | 77
1976-12-16 | 3211.36 |  |  | 91
1976-12-15 | 3211.38 |  |  | 91
1976-12-14 | 3211.38 |  |  | 91
1976-12-13 | 3211.38 |  |  | 80
1976-12-12 | 3211.35 |  |  | 64
1976-12-11 | 3211.35 |  |  | 64
1976-12-10 | 3211.35 |  |  | 64
1976-12-09 | 3211.33 |  |  | 64
1976-12-08 | 3211.33 |  |  | 65
1976-12-07 | 3211.28 |  |  | 66
1976-12-06 | 3211.23 |  |  | 66
1976-12-05 | 3211.23 |  |  | 57
1976-12-04 | 3211.2 |  |  | 50
1976-12-03 | 3211.18 |  |  | 50
1976-12-02 | 3211.1 |  |  | 50
1976-12-01 | 3211.05 |  |  | 49
1976-11-30 | 3211.05 |  |  | 59
1976-11-29 | 3211.06 |  |  | 64
1976-11-28 | 3211.07 |  |  | 64
1976-11-27 | 3211.07 |  |  | 86
1976-11-26 | 3211.1 |  |  | 97
1976-11-25 | 3211.12 |  |  | 97
1976-11-24 | 3211.15 |  |  | 97
1976-11-23 | 3211.18 |  |  | 98
1976-11-22 | 3211.18 |  |  | 98
1976-11-21 | 3211.18 |  |  | 63
1976-11-20 | 3211.1 |  |  | 48
1976-11-19 | 3211.05 |  |  | 49
1976-11-18 | 3211.02 |  |  | 48
1976-11-17 | 3210.99 |  |  | 48
1976-11-16 | 3210.93 |  |  | 48
1976-11-15 | 3210.93 |  |  | 48
1976-11-14 | 3210.92 |  |  | 162
1976-11-13 | 3211.01 |  |  | 240
1976-11-12 | 3211.19 |  |  | 240
1976-11-11 | 3211.31 |  |  | 244
1976-11-10 | 3211.42 |  |  | 245
1976-11-09 | 3211.51 |  |  | 245
1976-11-08 | 3211.66 |  |  | 245
1976-11-07 | 3211.8 |  |  | 245
1976-11-06 | 3211.95 |  |  | 200
1976-11-05 | 3212.1 |  |  | 145
1976-11-04 | 3212.2 |  |  | 145
1976-11-03 | 3212.23 |  |  | 145
1976-11-02 | 3212.35 |  |  | 145
1976-11-01 | 3212.4 |  |  | 200
1976-10-31 | 3212.4 |  |  | 245
1976-10-30 | 3212.6 |  |  | 245
1976-10-29 | 3212.78 |  |  | 245
1976-10-28 | 3212.93 |  |  | 245
1976-10-27 | 3213.1 |  |  | 245
1976-10-26 | 3213.16 |  |  | 245
1976-10-25 | 3213.3 |  |  | 245
1976-10-24 | 3213.43 |  |  | 245
1976-10-23 | 3213.59 |  |  | 245
1976-10-22 | 3213.73 |  |  | 245
1976-10-21 | 3213.92 |  |  | 245
1976-10-20 | 3214.05 |  |  | 245
1976-10-19 | 3214.21 |  |  | 245
1976-10-18 | 3214.36 |  |  | 244
1976-10-17 | 3214.53 |  |  | 244
1976-10-16 | 3214.7 |  |  | 244
1976-10-15 | 3214.85 |  |  | 244
1976-10-14 | 3215.06 |  |  | 244
1976-10-13 | 3215.2 |  |  | 246
1976-10-12 | 3215.36 |  |  | 246
1976-10-11 | 3215.52 |  |  | 246
1976-10-10 | 3215.7 |  |  | 246
1976-10-09 | 3215.91 |  |  | 246
1976-10-08 | 3216.03 |  |  | 246
1976-10-07 | 3216.24 |  |  | 246
1976-10-06 | 3216.39 |  |  | 246
1976-10-05 | 3216.5 |  |  | 246
1976-10-04 | 3216.6 |  |  | 246
1976-10-03 | 3216.7 |  |  | 246
1976-10-02 | 3216.84 |  |  | 246
1976-10-01 | 3216.99 |  |  | 246