## Sheet1
Evaporation Pond Water Data for the Brackish Groundwater National Desalination Research Facility
Parameter Name | Reporting Units | Human Health NPDWR/NSDWR MCL6 | NMAC 20.6.2.3103 8 | Pond-1 | [21 empty] | Pond-2 | [21 empty] | Pond-3
|  |  |  | 2012-06-13 |  | 2012-11-06 |  | 2013-07-16 |  | 2013-11-19 |  | 2014-12-01 |  | 2015-06-09 |  | 2015-12-08 |  | 2016-06-28 |  | 2016-12-06 |  | 2017-06-20 |  | 2017-12-05 |  | 2012-06-13 |  | 2012-11-06 |  | 2013-07-16 |  | 2013-11-19 |  | 2014-12-01 |  | 2015-06-09 |  | 2015-12-08 |  | 2016-06-28 |  | 2016-12-06 |  | 2017-06-20 |  | 2017-12-05 |  | 2012-06-13 |  | 2012-11-06 |  | 2013-07-16 |  | 2013-11-19 |  | 2014-12-01 |  | 2015-06-09 |  | 2015-12-08 |  | 2016-06-28 |  | 2016-12-06 |  | 2017-06-20 |  | 2017-12-05
General Chemistry
Collection Time | hour |  |  | 1030 |  | 925 |  | 954 |  | 800 |  | 900 |  | 800 |  | 800 |  | 800 |  | 800 |  | 800 |  | 900 |  | 1049 |  | 945 |  | 1010 |  | 900 |  | 930 |  | 900 |  | 900 |  | 830 |  | 830 |  | 830 |  | 930 |  | 1107 |  | 1005 |  | 1035 |  | 1000 |  | 1000 |  | 1000 |  | 1000 |  | 900 |  | 900 |  | 900 |  | 1000
Water Temperature | Degrees C |  |  | 26.5 |  | 15.6 |  | 24.4 |  | 11.3 |  | 2.4 | N | 24.1 | N | 4.60 | N | 25.5 | N | 7.5 | N | 27.4 | N | 11.6 | N | 28.7 |  | 14.5 |  | 27.1 |  | 11.2 |  | 7.3 | N | 23.3 | N | 4.40 | N | 26.2 | N | 6.6 | N | 26.1 | N | 10.1 | N | 27.4 |  | 14.5 |  | 26.3 |  | 11.2 |  | 3.3 | N | 22.8 | N | 6.00 | N | 24.7 | N | 6.2 | N | 25.1 | N | 11.2 | N
Dissolved Oxygen 1 | mg/L |  |  | 6.45 |  |  | v | 6.54 |  | 6.7 | [5 empty] | 12.76 |  | 5.58 |  | 10.3 | N |  |  | 8.55 | N | 6.18 |  | 8.95 |  | 4.87 |  | 6.46 | [5 empty] | 9.72 |  | 6.42 |  | 9.97 | N |  |  | 8.84 | N | 5.85 |  | 9.36 |  | 9.28 |  | 7.1 | [5 empty] | 10.52 |  | 5.68 |  | 10.73 | N |  |  | 9.14 | N
Alkalinity, Bicarbonate (as CaCO3) | mg/L CaCO3
Alkalinity, Carbonate | mg/L CaCO3
Alkalinity, Hydroxide | mg/L CaCO3
Total Alkalinity (as CaCO3) | mg/L CaCO3
P-Alkalinity (As CaCO3) mL of titrant | mL
pH – Aqueous | pH units | 6.5-8.5 | 6-9 | 8.27 | H | 8.48 | H | 8.62 | HX | 8.56 | HX | 8.41 |  | 8.49 |  | 9.10 |  | 8.52 |  | 8.47 |  | 8.53 |  | 8.27 |  | 8.2 | H | 8.6 | HX | 8.52 | HX | 8.55 | HX | 8.64 |  | 8.49 |  | 8.36 |  | 8.42 |  | 8.28 |  | 8.46 |  | 8.09 |  | 8.74 | HX | 8.52 | HX | 8.72 | HX | 8.83 | HX | 8.28 |  | 8.46 |  | 8.29 |  | 8.83 |  | 8.39 |  | 8.23 |  | 8.34
Color | Color Units | 15
Specific Conductance | µmhos/cm | [14 empty] | 57000 |  | 81200 |  | 45500 |  | 97000 |  | 20700 | [13 empty] | 18800 |  | 18900 |  | 21700 |  | 35500 |  | 9090 | [13 empty] | 19000 |  | 38800 |  | 24100 |  | 16900 |  | 19700
Bromide | mg/L
Chloride | mg/L | 250 | 250.0 | 7800 | X | 3300 | X | 5600 | X | 6700 |  | 5390 |  | 10800 |  | 8630 |  | 12900 |  | 9960 |  | 17700 |  | 3000 |  | 1500 | X | 17000 | X | 16000 | X | 20000 | X | 12200 |  | 2310 |  | 2030 |  | 2490 |  | 2940 |  | 5430 |  | 1050 |  | 8800 | X | 11000 | X | 15000 | X | 25000 |  | 11800 |  | 3590 |  | 2970 |  | 6510 |  | 3980 |  | 3390 |  | 3130
Cyanide | mg/L | 0.2 | 0.2 |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Fluoride | mg/L | 4.0/2.0 | 1.6 | 5.1 | X | 3 | Xv | 3.4 | Xv | 5.8 | X |  | U | 7.90 |  | 3.17 | J |  | U |  | U |  | U |  | U | 1.2 | J | 2.4 | Xv | 5.8 | X | 9.8 | X |  | U | 3.10 |  | 2.82 |  |  | U | 2.39 |  |  | U |  | U | 3.4 | Xv | 2.8 | Xv | 3.3 | Xv | 3.2 | Xv |  | U | 3.00 |  | 1.83 |  |  | U |  | U |  | U |  | U
Hardness, Total (as CaCO3) | mg/L
Langelier Saturation Index | SI
Nitrogen, Nitrate (as N) | mg/L | 10 | 10.0 | 3.4 | # |  | u |  | u |  | u |  | U |  | U | 0.152 | J |  | U | 2.26 | C |  | U | 6.44 |  |  | Hu |  | u |  | u |  | u |  | U |  | U |  | U | 2.17 |  |  | CU | 0.969 |  | 8.52 |  |  | u# |  | u |  | u |  | u |  | U |  | U |  | U |  | U | 0.447 | JC | 4.06 |  | 7.81
Nitrate+Nitrite (as N) | mg/L
Nitrogen, Nitrite (As N) | mg/L | 1
Nitrogen, Ammonia | mg/L
Perchlorate | mg/L
Phosphorus, Orthophosphate (as P) | mg/L
Phosphorus, Total (as P) | mg/L
Solids, Filterable Total Dissolved Solids | mg/L | 500 | 1000.0 | 34000 | X | 18500 | X | 30600 | X | 43200 | X | 24200 |  | 43700 |  | 44100 |  | 67400 |  | 32400 |  | 73000 |  | 17500 |  | 5400 | X | 77100 | X | 59200 | X | 101000 | X | 57900 |  | 9660 |  | 13700 |  | 9240 |  | 15400 |  | 24100 |  | 8200 |  | 47200 | X | 48600 | X | 27600 | X | 61000 | X | 33800 |  | 11000 |  | 13600 |  | 28700 |  | 17400 |  | 13900 |  | 16200
Sulfate | mg/L | 250 | 600.0 | 23000 | X | 8900 | X | 18000 | X | 21000 | X | 9770 |  | 21200 |  | 17600 |  | 24400 |  | 14500 |  | 30200 |  | 7040 |  | 2200 | X | 35000 | X | 31000 | X | 46000 | X | 26900 |  | 5350 |  | 6280 |  | 6890 |  | 7340 |  | 12600 |  | 3930 |  | 24000 | X | 31000 | X | 13000 | X | 21000 | X | 10500 |  | 4470 |  | 5140 |  | 10500 |  | 7030 |  | 5700 |  | 7080
Turbidity | NTU | 1-57
Metals and Major Cations
Aluminum | mg/L | 0.05-0.2 | 5.0 |  | u | 0.011 | J | 0.035 | v | 0.19 | X | 0.0637 |  | 0.0321 |  | 0.0380 |  | 0.0269 | J | 0.0138 | J | 0.119 |  | 0.0117 | J | 0.027 | v |  | u | 0.039 | v |  | u | 0.025 | J | 0.0217 | J | 0.0301 |  | 0.0189 | J | 0.0143 | J | 0.0163 | J | 0.0102 | J |  | u |  | u | 0.029 | v |  | u | 0.0948 |  | 0.0201 | J | 0.0979 |  | 0.0245 | J | 0.0137 | J | 0.0484 |  | 0.0128 | J
Arsenic | mg/L | 0.01 | 0.1 | 0.012 | X | 0.0063 | v | 0.0076 | J | 0.018 | JX | 0.00452 | J | 0.00876 |  | 0.00745 |  | 0.0103 |  | 0.00495 | J | 0.00859 |  | 0.00251 | J | 0.0016 | J | 0.027 | XH | 0.012 | X | 0.05 | JX | 0.0103 |  | 0.00397 | J | 0.00398 | J | 0.00330 | J | 0.00419 | J | 0.00527 |  |  | U | 0.013 | X | 0.013 | X | 0.0054 | J | 0.038 | JX | 0.00474 | J | 0.00341 | J | 0.00342 | J | 0.00552 |  | 0.00397 | J | 0.00258 | J | 0.00364 | J
Barium | mg/L | 2 | 1.0 | 0.05 | v | 0.032 | v | 0.036 | v | 0.05 |  | 0.027 |  | 0.0427 |  | 0.0386 |  | 0.0511 |  | 0.0237 |  | 0.0340 |  | 0.0151 |  | 0.0063 | v | 0.07 | v | 0.029 | v | 0.037 |  | 0.0351 |  | 0.0362 |  | 0.0119 |  | 0.0148 |  | 0.0163 |  | 0.0257 |  | 0.0127 |  | 0.024 | v | 0.021 | v | 0.087 | v | 0.17 |  | 0.0557 |  | 0.0386 |  | 0.0118 |  | 0.0276 |  | 0.0224 |  | 0.0225 |  | 0.0241
Boron | mg/L |  | 0.75 | 4.5 | v | 2.4 | v | 4.1 | v | 6.2 |  | 1.94 |  | 4.82 |  | 4.18 |  | 5.77 |  | 2.63 |  | 5.68 |  | 1.63 |  | 0.78 | v | 9.6 | v | 7.6 | v | 11 |  | 5.47 |  | 1.22 |  | 1.65 |  | 1.27 |  | 1.66 |  | 3.08 |  | 0.809 |  | 4 | v | 3.8 | v | 2.5 | v | 6 |  | 2.63 |  | 1.21 |  | 1.48 |  | 3.11 |  | 1.60 |  | 1.64 |  | 1.65
Cadmium | mg/L | 0.005 | 0.01 |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Calcium | mg/L
Chromium | mg/L | 0.1 | 0.05 |  | u |  | u |  | u | 0.0027 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.004 | J | 0.013 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.0021 | J | 0.016 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Cobalt | mg/L |  | 0.05 | 0.006 | J | 0.0033 | J | 0.0059 | J | 0.006 |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 0.002 | J | 0.013 | J | 0.008 | J | 0.015 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 0.0048 | J | 0.0082 | J | 0.0062 | v | 0.014 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Copper | mg/L | 1.3/1.0 | 1.0 | 0.083 | v |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U | 0.00229 | J |  | U | 0.016 | v |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 0.14 | v |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Iron (Dissolved) | mg/L | 0.3 | 1.0 | 0.016 | J | 0.014 | J | 0.011 | J |  | u | 0.0326 | J |  | U |  | U |  | U |  | U | 0.107 |  |  | U | 0.0036 | J | 0.019 | J |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 0.027 | v | 0.027 | v | 0.0097 | J |  | u |  | U |  | U | 0.0304 | J |  | U |  | U | 0.0807 | J |  | U
Iron (Total) | mg/L | 0.3 | 1.0
Lead | mg/L | 0.015 | 0.05 |  | u | 0.00023 | J |  | u | 0.00033 | J | 0.000304 | J |  | U | 0.000527 | J |  | U |  | U | 0.000434 | J |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Magnesium | mg/L
Manganese (Dissolved) | mg/L | 0.05 | 0.2 | 0.012 | v | 0.0064 | v | 0.0091 | v | 0.0083 | J | 0.00979 | J | 0.0543 |  | 0.0126 |  | 0.0393 |  | 0.00638 | J | 0.0951 |  | 0.0116 |  | 0.009 | v | 0.066 | XH | 0.044 | v | 0.02 |  | 0.0351 |  | 0.0345 |  | 0.0156 |  | 0.0138 |  | 0.0109 |  | 0.0744 |  | 0.00883 | J | 0.058 | X | 0.055 | X | 0.047 | v | 0.13 | X | 0.0306 |  | 0.0338 |  | 0.0199 |  | 0.0485 |  | 0.00562 | J | 0.0326 |  | 0.0145
Manganese (Total) | mg/L | 0.05 | 0.2
Mercury | mg/L | 0.002 | 0.002 | 4.5e-05 | J |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 3.7e-05 | J |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 4.6e-05 | J |  | u |  | u |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Molybdenum | mg/L |  | 1.0 | 0.1 | v | 0.052 | v | 0.055 | v | 0.084 |  | 0.0425 |  | 0.0483 |  | 0.0359 |  | 0.0460 |  | 0.0134 |  | 0.0233 |  | 0.00321 | J |  | u | 0.03 | J | 0.019 | v |  | u | 0.0409 |  | 0.0323 |  | 0.0211 |  | 0.00735 |  | 0.00831 |  | 0.00783 |  | 0.00266 | J | 0.019 | J | 0.012 | J |  | u |  | u | 0.0189 |  | 0.0263 |  | 0.0167 |  | 0.0105 |  | 0.00610 |  | 0.00471 | J | 0.00570
Nickel | mg/L |  | 0.2 |  | u |  | u | 0.0041 | J | 0.0052 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.0061 | J | 0.0091 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.0052 | J | 0.015 | J |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Potassium | mg/L
Selenium | mg/L | 0.05 | 0.05 | 0.019 | v | 0.0092 | v | 0.02 | v | 0.045 | J |  | U | 0.00405 | J | 0.00733 |  | 0.0117 |  | 0.0109 |  | 0.0100 |  | 0.00688 |  | 0.0034 | v | 0.041 | v | 0.03 | v | 0.098 | JX | 0.00513 |  |  | U |  | U | 0.00605 |  | 0.00333 | J | 0.00269 | J | 0.00526 |  | 0.028 | v | 0.03 | v | 0.014 | J | 0.056 | JX |  | U |  | U | 0.00202 | J | 0.00563 |  | 0.00525 |  | 0.00408 | J | 0.00504
Silicon Dioxide | mg/L
Silver | mg/L | 0.1 | 0.05 |  | u |  | u | 0.025 | J |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.016 | J |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  | u | 0.05 | J |  | u |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Sodium | mg/L
Strontium | mg/L
Uranium | mg/L | 0.03 | 0.03 | 0.11 | X | 0.018 | v | 0.046 | X | 0.071 | X | 0.013 | N | 0.0314 | N | 0.0194 | JN | 0.0238 | JN | 0.0124 | N | 0.0173 | N | 0.0162 | N | 0.0015 | J | 0.032 | XH | 0.035 | X | 0.04 | X | 0.0148 | N | 0.00749 | JN | 0.0110 | N | 0.0124 | JN | 0.00924 | JN | 0.00938 | JN | 0.0135 | N | 0.011 | J | 0.015 | v | 0.013 | v | 0.015 | J | 0.00769 | JN | 0.00654 | JN | 0.0129 | N | 0.0130 | JN | 0.00678 | JN | 0.00851 | JN | 0.0138 | N
Zinc | mg/L | 5 | 10.0 | 0.021 | J | 0.016 | v | 0.015 | v | 0.017 |  | 0.0199 |  | 0.00248 | J | 0.00592 |  | 0.00545 |  |  | U | 0.0212 |  | 0.00758 |  | 0.0042 | J | 0.023 | J | 0.023 | v | 0.032 | J | 0.00205 | J | 0.00223 | J |  | U | 0.00240 | J |  | U |  | U | 0.00670 |  | 0.034 | J | 0.019 | J | 0.018 | v | 0.03 | J | 0.0184 |  |  | U |  | U | 0.00220 | J |  | U | 0.0127 |  | 0.00432 | J
Radiology
Gross Alpha | pCi/L | 15 | [21 empty] | 92.3 | [21 empty] | 88.7 | [21 empty] | 83.3
Gross Alpha precision (±) | pCi/L | [22 empty] | 14.1 | [21 empty] | 14.1 | [21 empty] | 14.0
Radium-226 | pCi/L | 5 | 30 (Radium 226 and 228) | [20 empty] | -0.0103 | [21 empty] | 0.0475 | [21 empty] | 0.509
Radium-226 ± | pCi/L | [22 empty] | 0.354 | [21 empty] | 0.127 | [21 empty] | 0.405
Radium-228 | pCi/L | 5 | 30 (Radium 226 and 228) | [20 empty] | 1.12 | [21 empty] | 0.687 | [21 empty] | 0.583
Radium-228 ± | pCi/L | [22 empty] | 0.422 | [21 empty] | 0.420 | [21 empty] | 0.430
Organics
Organic Carbon, Total | mg/L | [6 empty] | 52 | p | [20 empty] | 110 | p | [20 empty] | 56 | p
VOCs
Benzene | µg/L | 5 | 10 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Bromodichloromethane | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Bromoform | µg/L |  |  | 1.3 | J |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Bromomethane | µg/L |  |  | 2.3 | J |  |  |  | u | [16 empty] | 2.1 | J |  |  |  | u | [16 empty] | 2.5 | J |  |  |  | u
Carbon Tetrachloride | µg/L | 5 | 10 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Chlorobenzene | µg/L | 100 |  | 1.2 | J |  |  |  | u | [16 empty] | 1.2 | J |  |  |  | u | [16 empty] | 1.2 | J |  |  |  | u
Chloroethane | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
2-Chloroethyl-vinyl ether | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Chloroform | µg/L |  | 100 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
cis-1,2-DCE | µg/L | 70 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
cis-1,3-Dichloropropene | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Dibromochloromethane | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
1,2-Dichlorobenzene | µg/L | 600 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
1,3-Dichlorobenzene | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
1,4-Dichlorobenzene | µg/L | 75 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
1,1-dichloroethane | µg/L |  | 25 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,2-dichloroethane (EDC) | µg/L | 5 | 10 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,1-dichloroethylene (1,1-DCE) 2 | µg/L | 7 | 5 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,2-Dichloropropane | µg/L | 5 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Ethylbenzene | µg/L | 700 | 750 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Methylene Chloride (DCM) | µg/L | 5 | 100 | 2 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 1.1 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,1,2,2-tetrachloroethane | µg/L |  | 10 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,1,2,2-tetrachloroethylene (PCE) 3 | µg/L |  | 20 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Toluene | µg/L | 1000 | 750 | 0.97 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 1.1 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 0.97 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Total Xylenes | µg/L | 10000 | 620 | 1.8 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U | 1.8 | J |  |  |  | u |  |  |  | U | 0.000362 | J |  | U |  | U |  | U |  | U |  | U | 1.8 | J |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
trans-1,2-Dichloroethene | µg/L | 100 |  |  | u |  |  |  | u | [16 empty] | 0.15 | J |  |  |  | u | [16 empty] | 0.16 | J |  |  |  | u
trans-1,3-Dichloropropene | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
1,1,1-trichloroethane | µg/L | 200 | 60 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,1,2-trichloroethane | µg/L | 5 | 10 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
1,1,2-trichloroethylene (TCE) 4 | µg/L | 5 | 100 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Trichlorofluoromethane | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Vinyl Chloride | µg/L | 2 | 1 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Acrolein | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Acrylonitrile | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Volatiles
Ethylene Dibromide (EDB) 5 | µg/L | 0.05 | 0.1 |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Phenolics
Phenols | µg/L |  | 5 |  | Hu |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU | 0.00121 | N |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU
Parent Acetanilides
PAHs: total naphthalene plus monomethylnaphthalenes | µg/L |  | 30
1-Methylnaphthalene | µg/L |  |  |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU
2-Methylnaphthalene | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  | 3.84e-05 | J |  | U |  | U |  | U |  | U |  | U |  | U
Naphthalene | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U | 0.0253 | J |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Benzo-a-pyrene | µg/L | 0.2 | .7 | 0.037 | v |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Synthetic Organics
Di(2-Ethylhexyl)adipate | µg/L | 400
Hexachlorocyclopentadiene | µg/L | 50 | [6 empty] | u | [21 empty] | u | [21 empty] | u
Atrazine | µg/L | 3 | [22 empty] | U | [21 empty] | U | [21 empty] | U
Alachlor | µg/L | 2
Hexachlorobenzene | µg/L | 1 | [6 empty] | u | [21 empty] | u | [21 empty] | u
Di(2-ethylhexyl)phthalate | ug/l | 6
Simazine | µg/L | 4
Pesticides and PCBs
4,4´-DDD | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
4,4´-DDE | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
4,4´-DDT | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Aldrin | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
alpha-BHC | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Polychlorinated biphenyls (PCBs) | µg/L | 0.5 | 1 |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | u |  |  |  | u |  |  |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU |  | NU
Aroclor 1016 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1221 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1232 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1242 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1248 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1254 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
Aroclor 1260 | µg/L |  |  |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U |  | u |  |  |  | u |  |  |  | U |  | U |  | U |  | U |  | U |  | U |  | U
beta-BHC | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Chlordane | µg/L | 2 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
delta-BHC | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Dieldrin | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endosulfan I | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endosulfan II | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endosulfan sulfate | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endrin | µg/L | 2 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endrin aldehyde | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Endrin Ketone | µg/L |  |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
gamma-BHC | µg/L | 0.2 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Heptachlor | µg/L | 0.4 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Heptachlor epoxide | µg/L | 0.2 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Methoxychlor | µg/L | 40 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Toxaphene | µg/L | 3 |  |  | u |  |  |  | u | [17 empty] | u |  |  |  | u | [17 empty] | u |  |  |  | u
Perfluorohexanoic Acid (PFHxA) | µg/L | [22 empty] | 0.0160 | N | [20 empty] | 0.00680 | N | [20 empty] | 0.0180 | N
Perfluoroheptanoic Acid (PFHpA) | µg/L | [22 empty] | 0.0310 | N | [20 empty] | 0.0100 | N | [20 empty] | 0.0250 | N
Perfluorooctanoic Acid (PFOA) | µg/L | [22 empty] | 0.490 | N | [20 empty] | 0.220 | N | [20 empty] | 0.350 | N
Perfluorononanoic Acid (PFNA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluorodecanoic Acid (PFDA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluoroundecanoic Acid (PFUnA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluorododecanoic Acid (PFDoA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluorotridecanoic Acid (PFTrDA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluorotetradecanoic Acid (PFTA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Perfluorobutanesulfonic Acid (PFBS) | µg/L | [22 empty] | 0.00650 | N | [20 empty] | 0.00470 | N | [20 empty] | 0.00900 | N
Perfluorohexanesulfonic Acid (PFHxS) | µg/L | [22 empty] | 0.0660 | N | [20 empty] | 0.0220 | N | [20 empty] | 0.0800 | N
Perfluorooctanesulfonic Acid (PFOS) | µg/L | [22 empty] | 0.0270 | N | [20 empty] | 0.0170 | N | [20 empty] | 0.0360 | N
N-methyl perfluorooctane-sulfonamidoacetic Acid (NMeFOSAA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
N-ethyl perfluorooctane-sulfonamidoacetic Acid (NEtFOSAA) | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
1,4-dioxane1 | µg/L | [23 empty] | NU | [21 empty] | NU | [21 empty] | NU
Thallium | mg/L | [23 empty] | U | [21 empty] | U | [21 empty] | U
Radon | pCi/L | [22 empty] | 8310 | [21 empty] | 1620 | [21 empty] | 565
Radon ± | pCi/L | [22 empty] | 48.8 | [21 empty] | 23.9 | [21 empty] | 17
Nomenclature:
u or U = concentration not detected at reporting limit
J = analyte detected below quantification limit
v = verified concentration
Z = Not Defined, or Zero
H = Holding times for preparation or analysis exceeded
X = Value exceeds maximum contaminant level
E = Value above quantitation range
# = Nitrate sample arrived at lab past holding time. Value from Nitrate+Nitrite analysis were substituted for Nitrate values because Nitrite was expected to be below detection.
N = Parameter not NELAC certified.
C = Sample result or QC discussed in the case narrative.
Footnotes:
1The Dissolved Oxygen analyses were performed by the staff of the Brackish Groundwater National Desalination Research Facility using a government-owned test kit and following the recommended procedures provided by Tetra Tech. Test results are included in this report.
2 1,1-Dichloroethene (International Union of Pure and Applied Chemistry (IUPAC) nomenclature)
3 Tetrachloroethene (International Union of Pure and Applied Chemistry (IUPAC) nomenclature)
4 Trichloroethene (International Union of Pure and Applied Chemistry (IUPAC) nomenclature)
5 1,2-Dibromoethane (International Union of Pure and Applied Chemistry (IUPAC) nomenclature)
6 NPDWS: National Primary Drinking Water Standards. NSDWS: National Secondary Drinking Water Standards. MCL: Maximum Contaminant Level
7 NPDWS states that for systems that use conventional or direct filtration, at no time can turbidity go above 1 NTU, and samples for turbidity must be less than or equal to 0.3 NTU in at least 95% of samples per month. Systems that use filtration other than conventional or direct filtration must follow state limits, which must include turbidity at no time exceeding 5 NTU.
8 New Mexico Administrate Code (NMAC) 20.6.2.3103 for ground water of 10,000 mg/l TDS or less.
Notes:
1. Analytes which were not requested and not analyzed for the sampling date are highlighted in dark gray.
2. Analyte concentrations exceeding NPDWS and NSDWS standards are underlined and in red font.
3. Analyte concentrations exceeding NMAC 20.6.2.3103 standards are highlighted in yellow.
4. Data from 3/15/2011 to 11/18/2013 obtained from Hall Environmental Analysis Laboratory in Albuquerque, New Mexico.
5. Data from 12/1/2015 and following obtained from DHL Analytical in Round Rock, Texas.
Notes Regarding Langelier Saturation Index (LSI):
1. The Langelier Saturation Index (sometimes Langelier Stability Index) is a calculated number used to predict the calcium carbonate stability of water. It indicates whether the water will precipitate, dissolve, or be in equilibrium with calcium carbonate. In 1936, Wilfred Langelier developed a method for predicting the pH at which water is saturated in calcium carbonate (called pHs). The LSI is expressed as the difference between the actual system pH and the saturation pH:
LSI = pH (measured) - pHs
For LSI > 0, water is super saturated and tends to precipitate a scale layer of CaCO3.
For LSI = 0, water is saturated (in equilibrium) with CaCO3. A scale layer of CaCO3 is neither precipitated nor dissolved.
For LSI < 0, water is under saturated and tends to dissolve solid CaCO3.
2. If the actual pH of the water is below the calculated saturation pH, the LSI is negative and the water has a very limited scaling potential. If the actual pH exceeds pHs, the LSI is positive, and being supersaturated with CaCO3, the water has a tendency to form scale. At increasing positive index values, the scaling potential increases.
3. In practice, water with an LSI between -0.5 and +0.5 will not display enhanced mineral dissolving or scale forming properties. Water with an LSI below -0.5 tends to exhibit noticeably increased dissolving abilities while water with an LSI above +0.5 tends to exhibit noticeably increased scale forming properties.
4. It is also worth noting that the LSI is temperature sensitive. The LSI becomes more positive as the water temperature increases. This has particular implications in situations where well water is used. The temperature of the water when it first exits the well is often significantly lower than the temperature inside the building served by the well or at the laboratory where the LSI measurement is made. This increase in temperature can cause scaling, especially in cases such as hot water heaters. Conversely, systems that reduce water temperature will have less scaling.